DRY PURY 11 – 13 – 17 – 21 – 25

Read the instructions carefully before operating or servicing the dehumidifier.

Observe all the safety instructions; failure to observe the instructions may lead to accidents and/or damage. Keep these instructions in a safe place for future reference.

V 04/21

Service Manual

Table of Contents

Part Ⅰ : Technical Information	12

1.Summary	12

2.Specifications	13

- Outline Dimension Diagram	17

- Refrigerant System Diagram	19

- Electrical Part	20

  - Wiring Diagram	20

  - PCB Printed Diagram	22

- Function and Control	24

  - Control Panel Instruction	24

  - Introduction of Basic Mode Function	26

Part Ⅱ : Maintenance	27

- Notes Maintenance	27

- Operation and maintenance	29

  - Drainage Method	29

  - Clean and Maintenance	29

  - Check Before Use-season	30

  - Care After Use-season	30

  - Long-time Storage	30

- Maintenance	31

  - Safety Principle of Maintenance	31

  - Preparation before Maintenance	31

  - Maintenance Cautions	32

  - Error Code	34

  - Malfunction Detection Flowchart	35

  - Maintenance Method for Common Malfunction	39

- Exploded View and Parts List	41

Table of Contents

## Removal Procedure	46

Appendix:	51

### Appendix 1: Reference Sheet of Celsius and Fahrenheit	51

### Appendix 2: Resistance Table of Temperature Sensor	52

### Appendix 3: Resistance Value Table of Humidity Sensor	57

#### Abbreviations Used Within this Manual:

| Abbreviation | Clear Words |
| --- | --- |
| OFDN | Oxygen free and dry nitrogen |
| PPE | Personnel protective equipment |
| LFL | Lower flammability level |
| UFL | Upper flammability level |
| HC | Hydrocarbon |

INTRODUCTION

ATTENTION

Please read this manual carefully before installing and operating the Hydrocarbon Air– Conditioner unit.

Careless installation and operation could cause severe injuries to operators, workers and damage to the air-conditioner unit itself.

Keep this manual in a location for easy access as it is needed for reference during installation, maintenance, service and operation of the unit.

This manual does not cover all aspects of installation, maintenance and service of the chiller units; if additional information is

needed, contact the ArgoclimaCostumer Service or Sales Office.

General Information

Warning and cautions appear at appropriate locations throughout this manual book.

Technical Information	1

Service Manual

Notices

General Safety Instructions

Please pay careful attention to these safety instructions, to avoid risks to people and property. Before starting work on maintenance read this manual thoroughly and pay particular attention to the relevant chapters.

Regardless of further requirements of the country, in which the equipment will be installed: assembly, first start up, technical service,

maintenance and repair and as well as dismantling and disposal have to be carried out by authorised personnel only.

During every operation strictly follow the instructions within this manual. Pay attention to the specific rules of air conditioning, electrics and refrigerant handling of the country within which the equipment is installed.

Key sections and/or sentences are highlighted with specific icons and symbols to the right side of the page. Please pay particular

attention to this information.

#### The Symbols Used in this Manual are as Follows

Information window highlighting important content of the specific section or additional information to consider.

This sign will indicate that you are handling a flammable substance and the surrounding environment can possibly contain it.

This is a general warning sign.

The Label is used to indicate that the flammable refrigerant is present within the application and service equipment.

Images that indicate something what you should strictly avoid.

2

Specific bans!       Specific commandments!       Instructions for first aid!       Fire protection!

Caref ully   read   t he

instructions!

Technical Information

Service Manual

Working on components with safety-relevant functions jeopardise the safe operation of   the installation. In case it is necessary to replace components, only use approved parts from Argoclima, the Original Equipment Manufacturer(OEM) or Argoclima released or authorised components. The system contains the refrigerant R-290 (propane). This condition requires special safety precautions to be observed. Maintenance for the system is strictly prohibited.At the installation site, no matter what kind of activities are executed, smoking is strictly prohibited!

Likewise, ensure the installation site is well ventilated. For further details as far as it concerns the handling of the refrigerant R-290 (propane) .

#### The Symbols Used in this Manual are as Follows

Electric operations (installation, repair, modification, maintenance, adjustment) have to be fulfilled by trained and authorised personnel only. When dealing with electrical issues, the specific rules of the country within which the equipment is installed must be followed, in addition to the instructions within this manual.

When working on the equipment or parts of it, the system has to be deenergised (by master switch, circuit breaker or separate cut-out) and made safe against restart of the system. Do not reconnect the system to the electric circuit until all work is done and all connections are tested. If handled unsafely or unprofessionally, severe electric shocks can occur. Consider the wiring diagram and follow the instructions of this manual very carefully whilst working on electrical parts. Wrong connections or incorrect grounding may lead to severe injuries and mortal danger.

Ground the system according to the particular requirements of the country within which the equipment is installed.

Connect all the wires properly and durably. Loose cables may lead to overheating or fire

#### Minimum Room Size

HC R290 is a fl	refrigerant and can form explosive mixtures in low concentrations. To minimise the risk of fire or explosion, the system must be installed in a room with a minimum floor area.

Unless there are further requirements, standards and legislation of the country within which the equipment is installed may apply. Any technicians that works on GREE hydrocarbon air– conditioners must be competent in the safe handling of flammable refrigerants, in addition to being in possession of knowledge and skills to maintain best refrigeration installation and servicing practices.

There are already training activities in place for engineers, technicians and sales staff to provide professional knowledge and skills for the handling of HC refrigerants and refrigeration systems operating with HCs.

Get trained and have your

“HC Refrigeration Professional” certification!

Technical Information	3

#### Basics in RAC

Knowledge of the basic SI standard units for temperature, pressure, mass, density, energy.

Service Manual

Understanding of the basic theory of refrigeration systems including the functions of the main components in the system (compressor, evaporator, condenser, thermostatic expansion valves).

Understanding how to read a refrigerant flow chart and an electrical circuit diagram.

The determination of non condensable gases in the refrigeration system and how to eliminate them.

The importance of the use of oxygen free dry nitrogen (OFDN) for system flushing, leak test and strength test.

The elimination of humidity from the refrigeration system and how to recover or vent HC refrigerant from a system.

Usage of tables and diagrams (log p/h diagram, saturation tables of a refrigerant, diagram of a single compression refrigeration cycle) and interpretation of these tables and diagrams.

Knowledge of the basic operation of the following components in a refrigeration system and their role and importance for refrigerant

leakage prevention and identification:

- Temperature and pressure controls

- Sight class and moisture indicators

- Defrost controls, reverse cycle operation

- System protectors

- Measuring devices such as the pressure gauge manifold

- Thermometer

- Leak detector

- Refrigerant charging devices

- Vacuum pump

- Oxygen free dry nitrogen cylinder and pressure regulator

Fault finding – analysis and repair.

- Knowledge of flammable refrigerants

- Risk analysis for the application of flammable refrigerant and properties of flammable refrigerants

- Electrical circuit assessment and repair

#### Checks before putting in operation, after a long period of nonuse, after maintenance or repair intervention or during operation.

Carry out a pressure and leak test to check the strength and the tightness of the system. Usage of a vacuum pump.

Evacuation of the system to remove air and moisture according to standard practice.

#### Checks for Leakage

Knowledge of potential leakage points of refrigeration, air-conditioning and heat pump equipment. Making a visual and manual inspection of the whole system.

Carry out a check for leakage of the system using an indirect method and/or one of the direct methods.

Direct leak detection methods:

- Fixed leakage detection systems

- Portable electronic gas detectors

3. Ultraviolet (UV) indication fluids

- Weak soapy water solution (bubble test) also in combination with OFDN

- New installation tightness test for leakage detection procedure e.g. H2/N2

- Operational system tightness test for leakage detection procedure

Indirect refrigerant detection methods:

- Visual

- Manual checks

Technical Information

4

Service Manual

HC R290 Refrigerant Lssues

Please notice that the unit is filled with propane. Details to this refrigerant are found in chapter “refrigerant”. Propane is highly flammable and leads to explosion under certain conditions. Inappropriate treatment of the unit involves the risk of severe damages of people and material.

#### Basics

HC R-290 (propane) is an odourless and colourless gas of the group of hydrocarbons.

HC R-290 is heavier than air and at high concentrations can cause narcotic effects and eventually asphyxiation.

R-290 is highly flammable within the range of 2,1% and 9,5% by volume, or 38

g/m3 to 170 g/m3 in air. The auto-ignition temperature is about 470°C.

Since R-290 is an odourless and colourless gas, it is difficult to perceive that it is

present (as with most other refrigerants).

Propane is often used as a fuel such as for heating or barbecues. However, for use on refrigeration systems, fuel-grade propane is not suitable since it contains high levels of impurities, which would damage the refrigeration system and may not provide the desired refrigerating capacity or efficiency.

### The structural formula of HC R-290 (propane)

#### Important  R efrigerant  P roperties  and Parameters:

Technical Information	5

Service Manual

Flammability

Three components are needed simultaneously for causing fire:

- Oxygen

- Ignition source

- The flammable concentration of HC

For ignition, the concentration of HC in air has to be between the lower and upper flammable limits. If the concentration is below the lower flammability limit (LFL) of about 2% by volume in air, there is not enough HC for combustion. If the concentration is above the upper fl	limit (UFL) of about 10% there is insuffi oxygen for combustion.

|  |  |  | Oxygen 0 % to 100 % |
| --- | --- | --- | --- |

2 %	10 %

HC R-290

Refrigerant

By way of illustration please compare to the schematic view:

Possible ignition sources are:

  - A flame, for example from brazing torch, halide torch leak lamp, match or lighter, cigarette

  - A spark from an electrical component

  - Static electricity

  - Hot surfaces

#### Safety Data

Hazard Identification

    - Extremely flammable (F+).

    - Readily forms an explosive air-vapour mixture at ambient temperatures.

    - Vapour is heavier than air and may travel to remote sources of ignition (e.g. along drainage systems, into basements etc).

    - Liquid releases generate large volumes of flammable vapour (approx 250:1)

    - Cold burns (frostbite) will result from skin / eye contact with liquid.

    - Liquid release or vapour pressure jets present a risk of serious damage to the eyes.

    - Abuse involving inhalation of high concentrations of vapour, even for short periods, which can produce unconsciousness or may prove fatal. Inhalation may cause irritation to the nose and throat, headache, nausea, vomiting, dizziness and drowsiness. In poorly ventilated areas unconsciousness or asphyxiation may result.

Technical Information

6

Service Manual

First Aid Measures

Inhalation:

Remove the affected person to fresh air. If breathing has stopped, administer artifi respiration. Give external cardiac massage if necessary. If the person is breathing but unconscious, place them in the recovery position. Obtain medical assistance immediately.

Skin:

In case of cold burns: flush with water to normalize temperature. Cover the burns with sterile dressings Do not use ointments or powders. Obtain medical assistance immediately.

Eyes:

Cold burns should be flushed with water to normalise temperature, cover the eye

with a sterile dressing and obtain medical assistance immediately.

#### Fire Fighting Measures

HC R-290 is delivered, stored, and used at temperatures above their flash point. Avoid all naked flames, sparks, cigarettes

etc.

- In case of fire, immediately alert fire brigade

- Ensure an escape path is always available from any fire

- If gas has ignited do not attempt to extinguish but stop gas flow and allowto burn out.

- Use water spray to cool heat-exposed containers, and to protect surroundingareas and personnel effecting the shut off

- Every precaution must be taken to keep containers cool to avoid the possibilityof a boiling liquid expanding vapour explosion (BLEVE)

#### Extinguishing Media:

In case of a large fire:

Release must be stopped and container cooled by water spray.

Water mist should be used to assist approach to the source of the fire. Large fires should only be handled by Fire Brigade.

### DO NOT USE WATER JET

Small fire:

Use dry powder extinguisher

Technical Information	7

### DO NOT USE WATER JET

Special protective equipment for fire fighters:

In confined spaces use self-contained breathing apparatus

Hazardous combustion products:

Incomplete combustion may form carbon monoxide.

Accidental Release Measures

Service Manual

Immediate emergency action:

  - Clear people away from the area to a safe place

  - Do not operate electrical equipment unless “Ex”-rated

  - Summon the emergency services

  - Treat or refer casualties if necessary

Further action (when release is made safe):

  - Extinguish all naked lights – avoid creating sparks

  - Position fire fighting equipment

  - Cover drains and disperse vapour with water spray.

Note: vapour may collectin confined spaces.

Further actions:

  - Stop release

  - Use dry powder or carbon dioxide extinguishers

  - Cool containers exposed to fire by using water / mist spray.

#### Accidental Release Measures

Due to the flammability of R-290 and the risk of fire or explosion during servicing, special safety rules must be followed during operation. In order to avoid damage for people and property, particular requirements are listed hereafter.

Before servicing the unit, the surrounding area were the work will be done must be clear of safety hazards to ensure safe working. Nevertheless it is required to carry out a risk assessment in order to minimise the risk of ignition of R-290.

The following safety measures must be followed:

1. Any employees and other present persons must be informed about the service and the way the service is done, first.

- It is recommended to isolate the working environment in order to keep out any unauthorised personnel.

- It is useful to set up signs such as „no smoking“ or „access denied“.

- It is prohibited to store any combustible goods within the working environment.

- Within two (2) metres radius, ignition sources are not allowed in the working area.

- Fire extinguisher (dry powder) must be easily accessible at any time.

- During service work, proper ventilation of the environment must be ensured.

Technical Information

8

Service Manual

Sign plate to protect and mark the working area.

Appropriate detectors, suitable for hydrocarbons, must be available and operational all the time. Appropriate tools and appliances must be available and ready for operation.

Any employees need to be instructed extensively about the safety measures and the possible safety hazard.

Gas Detection

While servicing the unit it is recommended for the whole period of work — before,during and after — to monitor the gas concentration in the air within the work environment. By monitoring the air within the work environment the danger of a possible formation of flammable atmosphere can be detected early.

Doing the monitoring, ensure that the gas detectors are suitable for hydrocarbon detection. Never use open fire or a device with an ignition source for the detection of gas or for leak detection.

Before operation of the gas detector the instruction manual must be read carefully. In case of any questions refer to the detector manufacturer. Furthermore ensure the detector is correctly calibrated. Instructions for calibration can be found in the instruction manual of the detector or upon request from the manufacturer.

A possible re-calibration must be done within an area which is free of refrigerants.

In case of a positive detection by the detector any work must be stopped immediately. Any open flames or ignition sources must be extinguished or removed. In addition to a suitable and approved HC gas detectors, portable gas detectors can be used.

Such a detector can be clipped to clothing or placed on the floor within the working area. It should be switched on for the duration of the work, and set to alarm at 15% of the lower flammability level (LFL), to warn that flammable concentration may be nearby. In this way, technicians can be alerted whenever an inadvertent release of fl	refrigerant occurs, and can immediately act upon the relevant emergency procedures.

Technical Information

Portable HC Gas Detector

9

Pressure—Temperature Chart

Service Manual

| HC Refrigerant R-290 |
| --- |
| Temperature | Absolute pressure | Gauge pressure |
| °C | °F | kPa | bar | PSI | kPa(g) | bar(g) | PSI(g) |
| -40 | -40 | 111,12 | 1,11 | 16,12 | 11,12 | 0,11 | 1,61 |
| -39 | -38,2 | 116,00 | 1,16 | 16,83 | 16,00 | 0,16 | 2,32 |
| -38 | -36,4 | 121,05 | 1,21 | 17,56 | 21,05 | 0,21 | 3,05 |
| -37 | -34,6 | 126,27 | 1,26 | 18,31 | 26,27 | 0,26 | 3,81 |
| -36 | -32,8 | 131,66 | 1,32 | 19,10 | 31,66 | 0,32 | 4,59 |
| -35 | -31 | 137,23 | 1,37 | 19,90 | 37,23 | 0,37 | 5,40 |
| -34 | -29,2 | 142,97 | 1,43 | 20,74 | 42,97 | 0,43 | 6,23 |
| -33 | -27,4 | 148,90 | 1,49 | 21,60 | 48,90 | 0,49 | 7,09 |
| -32 | -25,6 | 155,02 | 1,55 | 22,48 | 55,02 | 0,55 | 7,98 |
| -31 | -23,8 | 161,33 | 1,61 | 23,40 | 61,33 | 0,61 | 8,89 |
| -30 | -22 | 167,83 | 1,68 | 24,34 | 67,83 | 0,68 | 9,84 |
| -29 | -20,2 | 174,54 | 1,75 | 25,31 | 74,54 | 0,75 | 10,81 |
| -28 | -18,4 | 181,44 | 1,81 | 26,32 | 81,44 | 0,81 | 11,81 |
| -27 | -16,6 | 188,56 | 1,89 | 27,35 | 88,56 | 0,89 | 12,84 |
| -26 | -14,8 | 195,89 | 1,96 | 28,41 | 95,89 | 0,96 | 13,91 |
| -25 | -13 | 203,43 | 2,03 | 29,51 | 103,43 | 1,03 | 15,00 |
| -24 | -11,2 | 211,19 | 2,11 | 30,63 | 111,19 | 1,11 | 16,13 |
| -23 | -9,4 | 219,18 | 2,19 | 31,79 | 119,18 | 1,19 | 17,29 |
| -22 | -7,6 | 227,39 | 2,27 | 32,98 | 127,39 | 1,27 | 18,48 |
| -21 | -5,8 | 235,84 | 2,36 | 34,21 | 135,84 | 1,36 | 19,70 |
| -20 | -4 | 244,52 | 2,45 | 35,46 | 144,52 | 1,45 | 20,96 |
| -19 | -2,2 | 253,44 | 2,53 | 36,76 | 153,44 | 1,53 | 22,26 |
| -18 | -0,4 | 262,61 | 2,63 | 38,09 | 162,61 | 1,63 | 23,58 |
| -17 | 1,4 | 272,03 | 2,72 | 39,45 | 172,03 | 1,72 | 24,95 |
| -16 | 3,2 | 281,70 | 2,82 | 40,86 | 181,70 | 1,82 | 26,35 |
| -15 | 5 | 291,62 | 2,92 | 42,30 | 191,62 | 1,92 | 27,79 |
| -14 | 6,8 | 301,81 | 3,02 | 43,78 | 201,81 | 2,02 | 29,27 |
| -13 | 8,6 | 312,27 | 3,12 | 45,29 | 212,27 | 2,12 | 30,79 |
| -12 | 10,4 | 323,00 | 3,23 | 46,85 | 223,00 | 2,23 | 32,34 |
| -11 | 12,2 | 334,00 | 3,34 | 48,44 | 234,00 | 2,34 | 33,94 |
| -10 | 14 | 345,28 | 3,45 | 50,08 | 245,28 | 2,45 | 35,58 |
| -9 | 15,8 | 356,85 | 3,57 | 51,76 | 256,85 | 2,57 | 37,25 |
| -8 | 17,6 | 368,70 | 3,69 | 53,48 | 268,70 | 2,69 | 38,97 |
| -7 | 19,4 | 380,85 | 3,81 | 55,24 | 280,85 | 2,81 | 40,73 |
| -6 | 21,2 | 393,29 | 3,93 | 57,04 | 293,29 | 2,93 | 42,54 |
| -5 | 23 | 406,04 | 4,06 | 58,89 | 306,04 | 3,06 | 44,39 |
| -4 | 24,8 | 419,09 | 4,19 | 60,78 | 319,09 | 3,19 | 46,28 |
| -3 | 26,6 | 432,45 | 4,32 | 62,72 | 332,45 | 3,32 | 48,22 |
| -2 | 28,4 | 446,13 | 4,46 | 64,71 | 346,13 | 3,46 | 50,20 |
| -1 | 30,2 | 460,13 | 4,60 | 66,74 | 360,13 | 3,60 | 52,23 |
| 0 | 32 | 474,46 | 4,74 | 68,82 | 374,46 | 3,74 | 54,31 |
| 1 | 33,8 | 489,11 | 4,89 | 70,94 | 389,11 | 3,89 | 56,44 |
| 2 | 35,6 | 504,10 | 5,04 | 73,11 | 404,10 | 4,04 | 58,61 |
| 3 | 37,4 | 519,43 | 5,19 | 75,34 | 419,43 | 4,19 | 60,83 |
| 4 | 39,2 | 535,10 | 5,35 | 77,61 | 435,10 | 4,35 | 63,11 |
| 5 | 41 | 551,12 | 5,51 | 79,93 | 451,12 | 4,51 | 65,43 |
| 6 | 42,8 | 567,49 | 5,67 | 82,31 | 467,49 | 4,67 | 67,80 |
| 7 | 44,6 | 584,22 | 5,84 | 84,74 | 484,22 | 4,84 | 70,23 |
| 8 | 46,4 | 601,31 | 6,01 | 87,21 | 501,31 | 5,01 | 72,71 |
| 9 | 48,2 | 618,77 | 6,19 | 89,75 | 518,77 | 5,19 | 75,24 |
| 10 | 50 | 636,60 | 6,37 | 92,33 | 536,60 | 5,37 | 77,83 |

Technical Information

10

Service Manual

| HC Refrigerant R-290 |
| --- |
| Temperature | Absolute pressure | Gauge pressure |
| 11 | 51,8 | 654,81 | 6,55 | 94,97 | 554,81 | 5,55 | 80,47 |
| 12 | 53,6 | 673,40 | 6,73 | 97,67 | 573,40 | 5,73 | 83,17 |
| 13 | 55,4 | 692,38 | 6,92 | 100,42 | 592,38 | 5,92 | 85,92 |
| 14 | 57,2 | 711,75 | 7,12 | 103,23 | 611,75 | 6,12 | 88,73 |
| 15 | 59 | 731,51 | 7,32 | 106,10 | 631,51 | 6,32 | 91,59 |
| 16 | 60,8 | 751,68 | 7,52 | 109,02 | 651,68 | 6,52 | 94,52 |
| 17 | 62,6 | 772,25 | 7,72 | 112,01 | 672,25 | 6,72 | 97,50 |
| 18 | 64,4 | 793,24 | 7,93 | 115,05 | 693,24 | 6,93 | 100,55 |
| 19 | 66,2 | 814,64 | 8,15 | 118,16 | 714,64 | 7,15 | 103,65 |
| 20 | 68 | 836,46 | 8,36 | 121,32 | 736,46 | 7,36 | 106,82 |
| 21 | 69,8 | 858,71 | 8,59 | 124,55 | 758,71 | 7,59 | 110,04 |
| 22 | 71,6 | 881,39 | 8,81 | 127,84 | 781,39 | 7,81 | 113,33 |
| 23 | 73,4 | 904,51 | 9,05 | 131,19 | 804,51 | 8,05 | 116,69 |
| 24 | 75,2 | 928,07 | 9,28 | 134,61 | 828,07 | 8,28 | 120,10 |
| 25 | 77 | 952,07 | 9,52 | 138,09 | 852,07 | 8,52 | 123,58 |
| 26 | 78,8 | 976,53 | 9,77 | 141,64 | 876,53 | 8,77 | 127,13 |
| 27 | 80,6 | 1001,45 | 10,01 | 145,25 | 901,45 | 9,01 | 130,75 |
| 28 | 82,4 | 1026,83 | 10,27 | 148,93 | 926,83 | 9,27 | 134,43 |
| 29 | 84,2 | 1052,68 | 10,53 | 152,68 | 952,68 | 9,53 | 138,18 |
| 30 | 86 | 1079,00 | 10,79 | 156,50 | 979,00 | 9,79 | 141,99 |
| 31 | 87,8 | 1105,79 | 11,06 | 160,38 | 1005,79 | 10,06 | 145,88 |
| 32 | 89,6 | 1133,08 | 11,33 | 164,34 | 1033,08 | 10,33 | 149,84 |
| 33 | 91,4 | 1160,85 | 11,61 | 168,37 | 1060,85 | 10,61 | 153,87 |
| 34 | 93,2 | 1189,12 | 11,89 | 172,47 | 1089,12 | 10,89 | 157,97 |
| 35 | 95 | 1217,88 | 12,18 | 176,64 | 1117,88 | 11,18 | 162,14 |
| 36 | 96,8 | 1247,16 | 12,47 | 180,89 | 1147,16 | 11,47 | 166,38 |
| 37 | 98,6 | 1276,94 | 12,77 | 185,21 | 1176,94 | 11,77 | 170,70 |
| 38 | 100,4 | 1307,24 | 13,07 | 189,60 | 1207,24 | 12,07 | 175,10 |
| 39 | 102,2 | 1338,07 | 13,38 | 194,07 | 1238,07 | 12,38 | 179,57 |
| 40 | 104 | 1369,42 | 13,69 | 198,62 | 1269,42 | 12,69 | 184,12 |
| 41 | 105,8 | 1401,31 | 14,01 | 203,25 | 1301,31 | 13,01 | 188,74 |
| 42 | 107,6 | 1433,73 | 14,34 | 207,95 | 1333,73 | 13,34 | 193,44 |
| 43 | 109,4 | 1466,71 | 14,67 | 212,73 | 1366,71 | 13,67 | 198,23 |
| 44 | 111,2 | 1500,23 | 15,00 | 217,59 | 1400,23 | 14,00 | 203,09 |
| 45 | 113 | 1534,31 | 15,34 | 222,54 | 1434,31 | 14,34 | 208,03 |
| 46 | 114,8 | 1568,96 | 15,69 | 227,56 | 1468,96 | 14,69 | 213,06 |
| 47 | 116,6 | 1604,18 | 16,04 | 232,67 | 1504,18 | 15,04 | 218,17 |
| 48 | 118,4 | 1639,97 | 16,40 | 237,86 | 1539,97 | 15,40 | 223,36 |
| 49 | 120,2 | 1676,34 | 16,76 | 243,14 | 1576,34 | 15,76 | 228,63 |
| 50 | 122 | 1713,30 | 17,13 | 248,50 | 1613,30 | 16,13 | 233,99 |
| 51 | 123,8 | 1750,86 | 17,51 | 253,94 | 1650,86 | 16,51 | 239,44 |
| 52 | 125,6 | 1789,02 | 17,89 | 259,48 | 1689,02 | 16,89 | 244,98 |
| 53 | 127,4 | 1827,79 | 18,28 | 265,10 | 1727,79 | 17,28 | 250,60 |
| 54 | 129,2 | 1867,17 | 18,67 | 270,81 | 1767,17 | 17,67 | 256,31 |
| 55 | 131 | 1907,17 | 19,07 | 276,62 | 1807,17 | 18,07 | 262,11 |
| 56 | 132,8 | 1947,80 | 19,48 | 282,51 | 1847,80 | 18,48 | 268,01 |
| 57 | 134,6 | 1989,07 | 19,89 | 288,49 | 1889,07 | 18,89 | 273,99 |
| 58 | 136,4 | 2030,98 | 20,31 | 294,57 | 1930,98 | 19,31 | 280,07 |
| 59 | 138,2 | 2073,54 | 20,74 | 300,75 | 1973,54 | 19,74 | 286,24 |
| 60 | 140 | 2116,75 | 21,17 | 307,01 | 2016,75 | 20,17 | 292,51 |

Technical Information	11

# Part Ⅰ : Technical Information

Service Manual

## 1.Summary

DRY PURY 11

DRY PURY 13

DRY PURY 17

DRY PURY 21

DRY PURY 25

Technical Information

12

Service Manual

2.Specifications

| Model |  |  |  | DRY PURY 13 |
| --- | --- | --- | --- | --- |
| Product Code |  |  |  |  |
| Power Supply | Rated Voltage | V~ |  | 220-240 |
|  | Rated Frequency | Hz |  | 50 |
|  | Phases |  |  | 1 |
| Rated Dehumidification Capacity | L/h |  | 0.28 |
| Power Input | W |  | 210 |
| Current Input | A |  | 1.3 |
| Set Humidity Range | % |  | 30-80 |
| Air Flow Volume(H/M/L) | m3/h |  | 95/-/75 |
| Fan Motor Speed | r/min |  | 1080/900 |
| Fan Motor Power Output | W |  | 3 |
| Fan Motor RLA | A |  | 0.09 |
| Fan Motor Capacitor | μF |  | 1 |
| Fan Type |  |  | Centrifugal |
| Fan Diameter Length(DXL) | mm |  | Φ176X62 |
| Throttling Method |  |  | Capillary |
| Fuse Current | A |  | 3.15 |
| Sound Pressure Level(H/M/L) | dB (A) |  | 39/-/36 |
| Sound Power Level(H/M/L) | dB (A) |  | 52/-/49 |
| Climate Type |  |  | T1 |
| Isolation |  |  | I |
| Moisture Protection |  |  | IPX0 |
| Permissible Excessive Operating Pressure for the Discharge Side | MPa |  | 3 |
| Permissible Excessive Operating Pressure for the Suction Side | MPa |  | 1.5 |
| Dimension (WXHXD) | mm |  | 350X400X206 |
| Dimension of Carton Box(LXWXH) | mm |  | 389X248X422 |
| Dimension of Package(LXWXH) | mm |  | 392X251X437 |
| Application Area | m2 |  | 16 |
| Net Weight | kg |  | 12.5 |
| Gross Weight | kg |  | 13.5 |
| Refrigerant |  |  | R290 |
| Refrigerant Charge | kg |  | 0.050 |
| Bucket Capacity | L |  | 1.5/1.8 |
| Control Type |  |  | Electronic |
| Evaporator | Evaporator Form |  |  | Aluminum Fin-copper Tube |
|  | Evaporator Pipe Diameter | mm |  | Φ7 |
|  | Evaporator Row-fin Gap | mm |  | 2-1.4 |
|  | Evaporator Coil Length (LXDXW) | mm |  | 210X25.4X152.4 |
| Condenser | Condenser Form |  |  | Aluminum Fin-copper Tube |
|  | Condenser Pipe Diameter | mm |  | Φ5 |
|  | Condenser Rows-fin Gap | mm |  | 2-1.4 |
|  | Condenser Coil Length (LXDXW) | mm |  | 210X22.8X152.4 |
| Compressor | Compressor Manufacturer |  |  | Tatung Compressor(Zhongshan) CO.,LTD |
|  | Compressor Model |  |  | FX170M-E |
|  | Compressor Type |  |  | Reciprocating |
|  | Compressor Power Input | W |  | 230 |
|  | Compressor Overload Protector |  |  | HPA-106 |
|  | Compressor LRA. | A |  | 5.5 |
|  | Compressor RLA | A |  | 1.35 |

The above data is subject to change without notice; please refer to the nameplate of the unit.

Technical Information	13

Service Manual

| Model |  |  | DRY PURY 17 |
| --- | --- | --- | --- |
| Product Code |  |  |  |
| Power Supply | Rated Voltage | V~ | 220-240 |
|  | Rated Frequency | Hz | 50 |
|  | Phases |  | 1 |
| Rated Dehumidification Capacity | L/h | 0.37 |
| Power Input | W | 330 |
| Current Input | A | 2.0 |
| Set Humidity Range | % | 30-80 |
| Air Flow Volume(H/M/L) | m3/h | 120/-/110 |
| Fan Motor Speed | r/min | 1330/1150 |
| Fan Motor Power Output | W | 6 |
| Fan Motor RLA | A | 0.11 |
| Fan Motor Capacitor | μF | 1 |
| Fan Type |  | Centrifugal |
| Fan Diameter Length(DXL) | mm | Φ176X62 |
| Throttling Method |  | Capillary |
| Fuse Current | A | 3.15 |
| Sound Pressure Level(H/M/L) | dB (A) | 44/-/41 |
| Sound Power Level(H/M/L) | dB (A) | 56/-/- |
| Climate Type |  | T1 |
| Isolation |  | I |
| Moisture Protection |  | IPX0 |
| Permissible Excessive Operating Pressure for the Discharge Side | MPa | 3 |
| Permissible Excessive Operating Pressure for the Suction Side | MPa | 1.5 |
| Dimension (WXHXD) | mm | 350X400X206 |
| Dimension of Carton Box(LXWXH) | mm | 389X248X422 |
| Dimension of Package(LXWXH) | mm | 392X251X437 |
| Application Area | m2 | 22~28 |
| Net Weight | kg | 13 |
| Gross Weight | kg | 14 |
| Refrigerant |  | R290 |
| Refrigerant Charge | kg | 0.05 |
| Bucket Capacity | L | 1.5/1.8 |
| Control Type |  | Electronic |
| Evaporator | Evaporator Form |  | Aluminum Fin-copper Tube |
|  | Evaporator Pipe Diameter | mm | Φ7 |
|  | Evaporator Row-fin Gap | mm | 2-1.4 |
|  | Evaporator Coil Length (LXDXW) | mm | 210X25.4X152.4 |
| Condenser | Condenser Form |  | Aluminum Fin-copper Tube |
|  | Condenser Pipe Diameter | mm | Φ5 |
|  | Condenser Rows-fin Gap | mm | 2-1.4 |
|  | Condenser Coil Length (LXDXW) | mm | 210X22.8X152.4 |
| Compressor | Compressor Manufacturer |  | Tatung Compressor(Zhongshan) CO.,LTD |
|  | Compressor Model |  | FX250M-E |
|  | Compressor Type |  | Reciprocating |
|  | Compressor Power Input | W | 315 |
|  | Compressor Overload Protector |  | HPA-108 |
|  | Compressor LRA. | A | 7.1 |
|  | Compressor RLA | A | 1.9 |

The above data is subject to change without notice; please refer to the nameplate of the unit.

Technical Information

14

Service Manual

| Model |  |  | DRY PURY 21 | DRY PURY 25 |
| --- | --- | --- | --- | --- |
| Product Code |  |  |  |  |
| Power Supply | Rated Voltage | V~ | 220-240 | 220-240 |
|  | Rated Frequency | Hz | 50 | 50 |
|  | Phases |  | 1 | 1 |
| Rated Dehumidification Capacity | L/h | 0.83 | 0.51 |
| Power Input | W | 350 | 355 |
| Current Input | A | 1.8 | 1.9 |
| Set Humidity Range | % | 30-80 | 30-80 |
| Air Flow Volume(H/M/L) | m3/h | 170/-/145 | 220/-/155 |
| Fan Motor Speed | r/min | 960/840 | 1130/930 |
| Fan Motor Power Output | W | 5 | 12 |
| Fan Motor RLA | A | 0.118 | 0.168 |
| Fan Motor Capacitor | μF | 1 | 1.5 |
| Fan Type |  | Centrifugal | Centrifugal |
| Fan Diameter Length(DXL) | mm | Φ178.5X76.5 | Φ178.5X76.5 |
| Throttling Method |  | Capillary | Capillary |
| Fuse Current | A | 3.15 | 3.15 |
| Sound Pressure Level(H/M/L) | dB (A) | 39/-/37 | 44/-/42 |
| Sound Power Level(H/M/L) | dB (A) | 53/-/- | 56/-/- |
| Climate Type |  | T1 | T1 |
| Isolation |  | I | I |
| Moisture Protection |  | IPX0 | IPX0 |
| Permissible Excessive Operating Pressure for the Discharge Side | MPa | 3 | 3 |
| Permissible Excessive Operating Pressure for the Suction Side | MPa | 1.5 | 1.5 |
| Dimension (WXHXD) | mm | 360X482X244 | 360X482X244 |
| Dimension of Carton Box(LXWXH) | mm | 399X287X510 | 399X287X510 |
| Dimension of Package(LXWXH) | mm | 402X290X525 | 402X290X525 |
| Application Area | m2 | 30~36 | 36~42 |
| Net Weight | kg | 15.5 | 16 |
| Gross Weight | kg | 17 | 17 |
| Refrigerant |  | R290 | R290 |
| Refrigerant Charge | kg | 0.08 | 0.075 |
| Bucket Capacity | L | 2.6/3.0 | 2.6/3.0 |
| Control Type |  | Electronic | Electronic |
| Evaporator | Evaporator Form |  | Aluminum Fin-copper Tube | Aluminum Fin-copper Tube |
|  | Evaporator Pipe Diameter | mm | Φ7 | Φ7 |
|  | Evaporator Row-fin Gap | mm | 2-1.4 | 2-1.4 |
|  | Evaporator Coil Length (LXDXW) | mm | 238X25.4X190.5 | 238X25.4X190.5 |
| Condenser | Condenser Form |  | Aluminum Fin-copper Tube | Aluminum Fin-copper Tube |
|  | Condenser Pipe Diameter | mm | Φ5 | Φ5 |
|  | Condenser Rows-fin Gap | mm | 2-1.4 | 2-1.4 |
|  | Condenser Coil Length (LXDXW) | mm | 238X22.8X190.5 | 238X22.8X190.5 |
| Compressor | Compressor Manufacturer |  | Sichuan Danfu Environment Technology Co.,Ltd | Sichuan Danfu Environment Technology Co.,Ltd |
|  | Compressor Model |  | DFR60HF | DFR60HF |
|  | Compressor Type |  | Reciprocating | Reciprocating |
|  | Compressor Power Input | W | 318 | 318 |
|  | Compressor Overload Protector |  | HPA-110 | HPA-110 |
|  | Compressor LRA. | A | 11.49 | 11.49 |
|  | Compressor RLA | A | 1.8 | 1.8 |

The above data is subject to change without notice; please refer to the nameplate of the unit.

Technical Information	15

Service Manual

| Model |  |  | DRY PURY 11 |  |
| --- | --- | --- | --- | --- |
| Product Code |  |  |  |  |
| Power Supply | Rated Voltage | V~ | 220-240 |  |
|  | Rated Frequency | Hz | 50 |  |
|  | Phases |  | 1 |  |
| Rated Dehumidification Capacity | L/h | 0.21 |  |
| Power Input | W | 180 |  |
| Current Input | A | 1.1 |  |
| Set Humidity Range | % | 30-80 |  |
| Air Flow Volume(H/M/L) | m3/h | 95/-/75 |  |
| Fan Motor Speed | r/min | 1080/900 |  |
| Fan Motor Power Output | W | 3 |  |
| Fan Motor RLA | A | 0.09 |  |
| Fan Motor Capacitor | μF | 1 |  |
| Fan Type |  | Centrifugal |  |
| Fan Diameter Length(DXL) | mm | Φ176X62 |  |
| Throttling Method |  | Capillary |  |
| Fuse Current | A | 3.15 |  |
| Sound Pressure Level(H/M/L) | dB (A) | 39/-/36 |  |
| Sound Power Level(H/M/L) | dB (A) | 52/-/49 |  |
| Climate Type |  | T1 |  |
| Isolation |  | I |  |
| Moisture Protection |  | IPX0 |  |
| Permissible Excessive Operating Pressure for the Discharge Side | MPa | 3 |  |
| Permissible Excessive Operating Pressure for the Suction Side | MPa | 1.5 |  |
| Dimension (WXHXD) | mm | 350X400X206 |  |
| Dimension of Carton Box(LXWXH) | mm | 389X248X422 |  |
| Dimension of Package(LXWXH) | mm | 392X251X437 |  |
| Application Area | m2 | 12-16 |  |
| Net Weight | kg | 12 |  |
| Gross Weight | kg | 13 |  |
| Refrigerant |  | R290 |  |
| Refrigerant Charge | kg | 0.045 |  |
| Bucket Capacity | L | 1.5/1.8 |  |
| Control Type |  | Electronic |  |
| Evaporator | Evaporator Form |  | Aluminum Fin-copper Tube |  |
|  | Evaporator Pipe Diameter | mm | Φ7 |  |
|  | Evaporator Row-fin Gap | mm | 1-1.3 |  |
|  | Evaporator Coil Length (LXDXW) | mm | 210X12.7X152.4 |  |
| Condenser | Condenser Form |  | Aluminum Fin-copper Tube |  |
|  | Condenser Pipe Diameter | mm | Φ5 |  |
|  | Condenser Rows-fin Gap | mm | 2-1.4 |  |
|  | Condenser Coil Length (LXDXW) | mm | 210X22.8X152.4 |  |
| Compressor | Compressor Manufacturer |  | Sichuan Danfu Environment Technology Co.,Ltd |  |
|  | Compressor Model |  | DFR30HF |  |
|  | Compressor Type |  | Reciprocating |  |
|  | Compressor Power Input | W | 185 |  |
|  | Compressor Overload Protector |  | HPA-008 |  |
|  | Compressor LRA. | A | 5.65 |  |
|  | Compressor RLA | A | 1.1 |  |

The above data is subject to change without notice; please refer to the nameplate of the unit.

Technical Information

16

Service Manual

- Outline Dimension Diagram

DRY PURY 11

DRY PURY 13

DRY PURY 17

206

|  |  |  |  | 400 |
| --- | --- | --- | --- | --- |

350

unit:mm

Technical Information	17

Service Manual

DRY PURY 21

DRY PURY 25

244

360

unit:mm

Technical Information

18

Service Manual

- Refrigerant System Diagram

evaporator

air in

capillary

air out

condenser

fan motor

compressor

Dehumidifying principle of dehumidifier:

When temperature is decreased to the temperature point of dew, water vapor in humid air will condensate. Dehumidifier is

dehumidifying the air by using this principle.

During operation of the system, air will pass through evaporator and condenser in turn and then be discharged due to centrifugal blade. When the air is passing through evaporator, refrigerant will absorb the heat in air to let its temperature decrease to the temperature point of dew, water vapor in air will condensate. Condensate water comes into water tank through water tray, or is discharged directly through drainage hose. The saturated low-temperature air passed through the evaporator will absorb the heat when flowing along the condenser, and then become the dry air. Under normal condition, the nearby air will become warm during operation of dehumidifier.

Technical Information	19

Service Manual

- Electrical Part

### Wiring Diagram

●Instruction

| Symbol | Symbol Color | Symbol | Symbol Color | Symbol | Name |
| --- | --- | --- | --- | --- | --- |
| WH | White | GN | Green | COMP | Compressor |
| YE | Yellow | BN | Brown |  | Grounding wire |
| RD | Red | BU | Blue | / | / |
| YEGN | Yellow/Green | BK | Black | / | / |
| VT | Violet | OG | Orange | / | / |

DRY PURY 11

DRY PURY 13

DRY PURY 17

67	352;,0,7<

6:,7&+

02725

5'

&211(&725

%1	&

7(03 +80	&1

)$1

%1 %.

$3 ',63/$<

%2$5'

',63

',63

$3

$& /

1

/

%8 :+	1

<(*1 *1

57

78%(

78%(

0$,1 %2$5'

&203

%8

5'

32:(5

3(

7(03 6(1625

&

&203

<(*1

3(

&203

600007061299

Technical Information

20

Service Manual

DRY PURY 21

DRY PURY 25

These circuit diagrames are subject to change without notice ,please refer to the one supplied with the unit.

Technical Information	21

### PCB Printed Diagram

###### Silk Screen on Main Board

Service Manual

- Top view

1

  - Bottom view

Technical Information

22

Service Manual

Silk Screen on Display Board

- Top view

2

1

3

4

5

| No. | Name |
| --- | --- |
| 1 | Reserve WIFI needle stand |
| 2 | Interface of tube temperature sensor |
| 3 | Reserve the interface of discharge temperature sensor |
| 4 | Circuit interface of temperature/humidity inspection |
| 5 | Interface of main board |
| 6 | Reserve health function |

- Bottom view

Technical Information	23

- Function and Control

### Control Panel Instruction

Service Manual

Bucket full light indicates bucket needs to be emptied or it is not in the proper place

Filter Button

Display

Humidity Button

Notes:

    - Water bucket must be correctly installed for the dehumidifier to operate.

    - Do not remove the bucket while unit is in operation.

    - If you want to use drain hose to drain water away, please install the hose according to section "Drainage method".

    - Each time pressing the effective button on the control panel will give out a"beep" sound.

### Basic Functions of the Buttons

1 Power Button

Press this button to turn on/off dehumidifier.

Humdity Button

As for setting the humidify, after each pressing of humidify button, the set humidity will increase 5% in the range of 30%-80%

circularly; Hold the humidify button can adjust the humidity quickly.

3 Fan Button

Press this button can freely switch from high fan speed to low fan speed. When you need fast dehumidification, select high

fan speed; when you need the unit to work quietly, select low fan speed.

Timer Button

Press this button can make the unit work on designated time. The timer function takes hour as unit, and 0-24h can be circularly set. Duration of timer can be transitorily displayed on the panel.

Filter Button

Press this button to turn off Filter Cleaning lndicator.(When dehumidifi	has been operating for 250 hours, Filter Cleaning Indicator will be lit up to remind user of filter cleaning).

Technical Information

24

Service Manual

Auto Button

After pressing auto button, the unit enters into or exit from auto dry mode. When entering into auto dry mode, the unit will automatically set the comfortable humidity for users.

Note: under auto dry mode, adjust the set humidity will exit from this mode.

Display

The humidity display window is defaulted to display current environment humidity. If press humidity button to adjust the humidity, it will display the set humidity. 5s later, it will turn back to display the ambient humidity.

### Other Instructions

- Alarm Warning

If bucket is full or not locked into place for over 3min, buzzer will beep for 10s to remind you to empty bucket or put it back into the correct place.

- Auto Stop

When bucket is full, removed or not placed correctly or the humidity is 5%lower than the set humidity, unit will automatically stop.

- Memory Function

If power is lost, all of the control settings are remembered. So when power is restored, the unit will start back up in the settings it was in when power was lost.

- Bucket full light

This indicates that bucket is full or removed or not placed correctly.

- Clean the Filter On indicator light

When dehumidifier has been operating for 250 hours,Filter Cleaning lndicator will be lit up to remind user of filter cleaning.

Technical Information	25

Service Manual

### Introduction of Basic Mode Function

- System Basic Function

Adjustment of humidity takes 5% as a unit, user can select circularly within 30%~80%. The set humidity is always

displayed on the control panel

  - When HUMIDITYpreset ≤ HUMIDITYamb.-5%,compressor and fan will run.

  - When HUMIDITYpreset ≥ HUMIDITYamb.+5%,compressor stop to run and fan will stop operation after 3min.

  - When HUMIDITYamb.-5% ＜ HUMIDITYpreset ＜ HUMIDITYamb.+5%,when compressor is operation,it will run with condition a;when compressor stops,it will run with condition b;If under this condition when the unit is on,the compressor is off and fan will stop to run after 3min delay.

- Protection Function

- Working temperature range

- Detect the unit after energized, when 2℃ ≤Tamb. <37℃ , the unit is running normally; when Tamb. <2℃ or Tamb. ≥

37℃ , the compressor stops, and fan will run with the detected temperature humidity;

- During operation, when Tamb. <2℃ or Tamb.≥37℃ , the compressor stops, and fan will run with the detected temperature humidity;when 2℃ ≤Tamb. <37℃ , the compressor will be started up.

- Compressor protection

- After energization, under any situation and after compressor stops, it will restart 3min delay at least.

- Under operation state except temperature sensor malfunction, on/off button, water-blow protection, after compressor starts up, it will stop after it runs for 3mins at least.

- Detection for temperature sensor malfunction

When there's malfunction for temperature sensor, compressor and fan stop operation. LED indicator is OFF and buttons are invalid.

Nixie tube displays F2. After the temperature is resumed normally, restart the unit.

- Water blow protection (off switch)

- The water blow protection will be occurred when the water level of water tank is exceeded. After water blow protection, compressor stops and fan stops after 3mins. If water blow protection occurred for 3min, the buzzer will stop after it gives out a beep for 10s,indicator of water blow will blinks and all the buttons are invalid except power button. When the water level or assembly of water tank resume to normal,signal of water blow protection will cancelled, indicator is off, buzzer stops to give out a beep and resume to normal operation state.

- When the unit is off, water blow protection is occurred, water blow indicator blinks, compressor and fan stops, all the buttons are invalid except on/off buttons. When the unit is on, water blow indicator blinks, buzzer will not give out a beep, compressor and fan stops.

- Other Functions

Power-off memory:Upon power failure, the unit after power recovery will automatically start to run according to memory content.

Technical Information

26

Service Manual

Part Ⅱ : Maintenance

7.Notes Maintenance

Safety Precautions: Important!

Please read the safety precautions carefully before maintenance：

The following contents are very important for installation and maintenance.

Please follow the instructions below.

- The maintenance must accord with the instructions.

- Comply with all national electrical codes and local electrical codes.

- Pay attention to the warnings and cautions in this

manual.

- Be caution during maintenance. Prohibit incorrect operation to prevent electric shock and other accidents.

Warnings

When refrigerant leaks or requires discharge during installation, maintenance, or disassembly, it should be handled by certified professionals or otherwise in compliance with local laws and regulations.

- This unit adopts R290 refrigerant. System maintenance is strictly prohibited.

- If the refrigerant leaks or the pipeline is damaged, it is forbidden to conduct the maintenance. The unit should be recycled and disposed according to local regulations.

- It is strictly forbidden to cut or weld the refrigerant. Otherwise, it may lead to explosion.

  - Cut off the power supply before maintenance.

  - Specialized circuit must be applied; prohibit sharing the same circuit with other electric appliances; protection switch must be installed.

  - Have the unit adequately grounded. The grounding wire cant be used for other purposes.

  - The live wire, neutral wire and grounding wire of power sup- ply must be corresponding to the live wire, neutral wire and grounding wire of the dehumidifier.

  - The power cord cant be pressed by hard objects.

  - If the power cord or connection wire is not long enough, please get the specialized power cord or connection wire from the manufacture or distributor. Prohibit prolong the wire by yourself.

7. Replace the fuse with a new one of the same specification if it is burnt down; dont replace it with a cooper wire or conduct- ing wire.

- Use the power supply with same voltage and frequency as shown in rating label.

- Do not pull out the power plug when the unit is operating to avoid damaging the circuit.

10. Do not place anything at the top of dehumidifier; ensure the air outlet or air inlet is not blocked; do not use the unit near wall and curtain.

11. Do not use heating equipment around the unit.

Maintenance	27

Service Manual

Appliance filled with flammable gas R290.

Before install and use the appliance, read the owner’s manual first. Before install the appliance, read the installation manual first.

Before repair the appliance, read the service manual first.

The Refrigerant

To realize the function of the air conditioner unit, a special refrigerant circulates in the system. The used refrigerant is the fluoride R290, which is specially cleaned.

The refrigerant is flammable and inodorous. Furthermore, it can leads to explosion under certain conditions. Compared to common refrigerants, R290 is a nonpolluting refrigerant with no harm to the ozonosphere.

The influence upon the greenhouse effect is also lower. R290 has got very good thermodynamic features which lead to a really high energy efficiency. The units therefore need a less filling.

Please refer to the nameplate for the charging quantity of R290.

WARNING

Appliance filled with flammable gas R290.

Appliance shall be installed, operated and stored in a room with a floor area larger than 4m2.

The appliance shall be stored in a room without continuously operating ignition sources . (for example: open flames, an operating gas appliance or an operating electric heater.)

The appliance shall be stored in a well-ventilated area where the room size corresponds to the room area as specified foroperation.

The appliance shall be stored so as to prevent mechanical damage from occurring.

Ducts connected to an appliance shall not contain an ignition source.

Keep any required ventilation openings clear of obstruction. Do not pierce or burn.

Be aware that refrigerants may not contain an odour.

Do not use means to accelerate the defrosting process or to clean, other than those recommended by themanufacturer.

Servicing shall be performed only as recommended by the manufacturer. Should repair be necessary, contact your nearest authorized Service Centre. Any repairs carried out by unqualified personnel may be dangerous.

Compliance with national gas regulations shall be observed. Read specialist’s manual.

28	Maintenance

Service Manual

- Operation and maintenance

### Drainage Method

Option 1 Emptying Manually

Note:

- Do not remove the bucket when unit is in operation or has just stopped.Otherwise it may cause some water to drip on the floor.

- Do not use the hose if using water bucket to collect water. When the hose is  connected, water will be drained out through it instead of into the bucket.

- Hold the handles on both sides of the water bucket and pull it out following the arrow direction. (Attention: Pull out the bucket carefully in case the water may spill out from the bucket and onto

the floor.)

- Pour out the water inside the water tank.

- Replace bucket in the dehumidifier according to the arrow direction.

Option 2 Gravity Drain Hose

- Hose is not provided, so user shall prepare it in advance.	[Size: The hose should have an inner diameter  of 14mm]

- Unscrew the drain cover, and pull out the rubber plug from the unit as instructed.

3. Take out the adaptor and connect it firmly to the continuous

drainage port.

- Thread the drain hose onto the adaptor and make sure it's securely locked.

Maintenance

- Replace the bucket. Make sure the drain hose goes through the buckets drain hole and is placed downward.Lead the hose to the fl drain and the cover the hole with a lid. Note that drain hose should not be pressed, otherwise water can not be drained out.

Note: When you want to take off the drain hose, prepare a receptacle to collect water from the nozzle.

### Clean and Maintenance

Warning:

- Berore cleaning,turn off the dehumidifier and disconnect power.

Otherwise it may lead to electric shock.

- Do not wash the dehumidifier with water,or it may lead to electric shock.

- Do not use volatile liquid(such as thinner or gasoline) to clean

dehumidifier.Otherwise it will damage units appearance.

- Grille and Case

To clean the case:When there is dust on the case, use soft towel to dust it off; When the case is very dirty(greasy),use mild detergent to clean it.To clean the grille:Use a dust catcher or brush.

29

Service Manual

- Filter

The filter should be checked and cleaned at least every 250 hours of

operation or more often if necessary.

To remove:Press the “PUSH” above the filter with two hands

simultaneously, then the filter can be removed.

To clean:Clean the filter in warm,soapy water.Rinse it and let the

filterdry before replacing it.

Warning:

- Do not operate the dehumidifier without a filter.Otherwise the evaporator will catch dust and affect units performance.

- Do not dry the air filter with fire or electric hair dryer.Otherwise the air filter may be unshaped or caught on fire.

- Dont use dust catcher or brush to clean the air filter.Otherwise the air filter may be destroyed.

### Check Before Use-season

- Check whether air outlet is blocked.

- Check whether power plug and power socket are in good

condition.

- Check whether air fillter is clean.

- Check whether drain hose is damaged.

### Care After Use-season

- Disconnect power.

- Clean air filter and case.

- Clean dust and obstacle of the dehumidifier.

- Empty the water bucket.

### Long-time Storage

If you wnot use the dehumidifier for a long time ,we suggest that you

follow the steps below in order to maintain the unit in good condition.

- Make sure the bucket is clear of water and drain hose is removed.

- Clean the unit and wrap it well to prevent the gathering of dust.

30	Maintenance

Service Manual

## 9.Maintenance

### Safety Principle of Maintenance

1. The maintenance spot must have good ventilation. Do not close the door or the window.

2. Do not use naked flame, including welding, smoking. Do not use power tools.Do not use mobile phone. Tell the user not to cook with naked flame.

3. Take antistatic measures, including wearing pure cotton clothes and gloves etc.

4. If flammable refrigerant leakage is found during maintenance,it is a must to reinforce ventilation and take effective protective measures.

- During maintenance, it is necessary to keep the spot safe when fetching the lacked spare parts.

- It is necessary to keep the case of the air conditioner grounded during maintenance.

- The maintenance irrelated to refrigerant vessel, inner refrigerant pipe and cooling component can be performed in the user’s place, including cleaning the cooling system and sludging.

- Ensure that the density tester is working during maintenance.

- Ensure there is necessary safety precaution and emergency measures on the spot. Put suitable fire extinguishers(CO2 or dry powder) in

the nearest area.

- There must be natural ventilation in the maintenance spot.

- The maintenance staff shall take safety actions.

- Paste suitable signs such as “No Smoking” and “No Entry”.

### Preparation before Maintenance

- Inspection of Environment

- Ensure that electric product with radiation is power off in the maintenance area. All the persons in the room shall turn off the mobile phone.

- Check if there is refrigerant leakage in the maintenance area. Ensure that all the leak testers are suitable for this air conditioner.

- Ensure that the room area reaches the requirement.

- Check if the maintenance area is ventilated. Keep the room ventilated.

- Inspection of Air Conditioner

- Ensure that the air conditioner is reliably grounded.

- Ensure that the power supply of the air conditioner is cut off. Discharge the electricity of the capacitor. If power supply is necessary, perform leak test to prevent the potential danger.

- Inspection of Maintenance Equipment

(1) Check if the maintenance equipment is suitable for the refrigerant. Only the special equipment recommended by the air conditioner supplier can be used.

(2) The set alarm density of the leak tester shall not be higher than 25% of the LEL. The tester must keep operating during maintenance.

- Leak Test before Maintenance

(1) After cutting off the power supply, perform leak test with the recommended leak detector or density tester (pump suction type) (ensure the equipment is calibrated; leakage ratio of leak detector is 2g/year.)

Note: do not use resolvent with chlorine in case causing corrosion of the steel pipe.

(2) If leakage is found, remove all fire source ensure good ventilation of the area.

- Check List

| No. | Check information | Result | Yes/No |
| --- | --- | --- | --- |
| 1 | Maintenance equipment is complete |  |  |
| 2 | Persons in the maintenance area turn off the mobile phone. |  |  |
| 3 | Power supply of tools is 2m away. |  |  |
| 4 | Density tester can be used. |  |  |
| 5 | Other tools are normal. |  |  |
| 6 | Maintenance staffs are qualified. |  |  |
| 7 | The spare parts are provided by the manufacturer and qualified. |  |  |
| 8 | The air conditioner needed to be serviced is under safe state. |  |  |
| 9 | The wire of power socket is reliably connected. |  |  |
| 10 | There is natural ventilation in maintenance area. |  |  |
| 11 | There is no operating electric appliance or naked flame within 2m of Maintenance area. |  |  |

Maintenance	31

Service Manual

### Maintenance Cautions

If it is necessary to replace components, all the components used shall be made by manufacturer. Otherwise, the supplier shall not bear the responsibility.

- Maintenance of Electrical Parts

(1)Replace the power cord and connecting wire with that of the same specification.

- When inspecting the circuit with power on, check if there is electric leakage for the metal component such as evaporator or condenser. During inspection, do not touch the circuit so as to prevent electric shock.

- When inspecting the capacitor, ensure that the maintenance area is well ventilated. After conforming there is no refrigeration leakage, discharge electricity of capacitor.

- Before replacing the component, cut of the power supply of the air conditioner.

(5)Cut off the power before disconnecting and connecting the wire. Disconnect the live wire first and then ground wire. (6)During maintenance, do not remove the protective component. Use the component of same supplier and specification.

(7)When servicing the hermetic parts, cut of the power of the air conditioner before opening the sealing cover. If it is necessary to use power

supply, perform leak test to prevent potential danger.

- Do not replace the case which may affect the protective grade.

- Ensure that the sealing material is not degraded and that it can prevent entry of flammable gas. The parts used for replacement must

reach the requirement of the suppler.

(1).Replace electric box

- Maintenance of Refrigeration System

Before the maintenance, check whether there is any leakage or blockage in the refrigeration system. If yes, it is forbidden to conduct the maintenance. The unit should be recycled and disposed according to local regulations.

32	Maintenance

Service Manual

(2).Replace main board

Maintenance	33

Service Manual

### Error Code

| No. | Malfunction Name | DisplayCode | Unit status | Possible Causes |
| --- | --- | --- | --- | --- |
|  |  | Display Window |  |  |
| 1 | Ambient Temperature Sensor Malfunction | F1 | Compressor and fan motor stop. | Ambient temperature sensor is loosen or is poorly connected with the terminal of display board. Some element of display board may have been put upside down and cause short circuit. Ambient temperature sensor is damaged(Please refer to Checking Table for Temperature Sensor Resistance). Display board is damaged. |
| 2 | TubeTemperature Sensor Malfunction | F2 | Compressor and fan motor stop. Buttons are invalid. | Temperature sensor on the evaporator is loosen or is poorly connected with the terminal of display board. Some element of display board may have been put upside down and cause short circuit. Temperature sensor on the evaporator is damaged (Please refer to Checking Table for Temperature Sensor Resistance). Display board is damaged. |
| 3 | Humidity Sensor Malfunction | L1 |  | Humidity sensor is short-circuited. Humidity sensor is damaged. Display board is damaged. |
| 4 | Insufficient Refrigerant protection | F0 | The compressor stops,the fan motor stop after 30s later. | Refrigerant is leaking. System is blocked. |
| 5 | High-temperature overoad protection | H3 |  | Ambient operation condition is bad. The evaporator and condenser are blocked with filth. The system is abnormal. |

34	Maintenance

Service Manual

### Malfunction Detection Flowchart

- Malfunction of temperature sensor F1, F2

Maintenance	35

Service Manual

- Malfunction of humidity sensor L1

36	Maintenance

Service Manual

3. Malfunction of Insufficient Refrigerant protection F0

Maintenance	37

Service Manual

4. High-temperature overload protection H3

38	Maintenance

Service Manual

### Maintenance Method for Common Malfunction

- The Unit Can't Start Up

| Possible causes | Discriminating method (dehumidifier status) | Troubleshooting |
| --- | --- | --- |
| No power supply, or poor connection for power plug | After energization, operation indicator isnt bright and the buzzer can't give out sound | Confirm whether its due to power failure. If yes, wait for power recovery. If not, check power supply circuit and make sure the power plug is connected well. |
| Poor connection between wiring terminals | Power indicator is not on after the unit is energized | Check the circuit according to wiring diagram and connect wire properly; ensure each wiring terminal contact firmly |
| There is electric leakage in the unit | Circuit breaker jump off immediately after the unit is energized | Make sure the unit is properly grounded; Make sure the wiring is correct; Check if the insulating layer of wires inside the unit and power cord is in good condition; if the layer is broken, please replace it. |
| Placing position of water tank is not correct. Water is removed or the water is full. | Wall-full indicator flashes. | Make sure the water tank is placed correctly. |

- Poor Dehumidifying Effect

| Possible causes | Discriminating method (dehumidifier status) | Troubleshooting |
| --- | --- | --- |
| Filter is blocked | Check the filter to see its blocked | Clean the filter |
| Placing position of water tank is improper. | Check whether therere obstacles around the dehumidifier blocked the air outlet. | Make sure therere no obstacles around the dehumidifiers. |
| Refrigerant is leaking | Air outlet temperature is lower than normal temperature during dehumidifying period. | Find out the cause of leakage and solve the problem; charge refrigerant |
| Malfunction of capillary | Air outlet temperature is lower than normal temperature during dehumidifying period. If the refrigerant isnt leaking, some parts of capillary is blocked. | Replace capillary |
| Malfunction of fan | Fan can't operate. | Refer to point 3 of maintenance method for details |
| Malfunction of compressor | Compressor can't operate | Refer to point 4 of maintenance method for details |

- Fan Can't Operate

| Possible causes | Discriminating method (dehumidifier status) | Troubleshooting |
| --- | --- | --- |
| Wrong wire connection, or poor connection | Check the wiring status according to circuit diagram | Connect wires according to wiring diagram to make sure all wiring terminals are connected firmly |
| Needle stand of connection wire between mainboard and display board is loosened | Check if the needle stand is loosened | Reinsert the needle stand firmly |
| Fan capacitor is broken | Test the voltage between two ends of fan capacitor with universal meter and the value is 0 | Replace fan capacitor |
| Power supply voltage is too low or too high | Test the power supply voltage with universal meter and the value is too high or too low | Apply voltage regulator |
| Fan is broken | The above situation is normal but the fan does not operate | Repair or replace the fan |

Maintenance	39

Service Manual

- Compressor Can't Operate

| Possible causes | Discriminating method (dehumidifier status) | Troubleshooting |
| --- | --- | --- |
| Wrong wire connection, or poor connection | Check the wiring status according to circuit diagram | Connect wires according to wiring diagram to make sure all wiring terminals are connected firmly |
| Compressor relay on the mainboard is broken or the compressor needle stand is loosened | Check if the relay is sucked in cooling mode | Replace the mainboard with the same model |
| Power voltage is a little low or high | After turning on the unit, dehumidifying effect is poor or compressor is turned on or off frequently. Use universal meter to measure the power supply voltage directly | The fluctuation of voltage is 10% rated power. If the power is too low or too high, you are suggested to equip wit voltage regulator. |

- Water Leakage

| Possible causes | Discriminating method (dehumidifier status) | Troubleshooting |
| --- | --- | --- |
| Drainage pipe hasnt been installed correctly. | Water is coming out from indoors. | Eliminate the blocking objects inside the drainage channel. |

- Abnormal Sounds and Vibration

| Possible causes | Discriminating method (dehumidifier status) | Troubleshooting |
| --- | --- | --- |
| There is abnormal sound in some parts when just turning on or turning off the unit | Theres the sound of "PAPA" | Normal phenomenon. Abnormal sound will disappear after a few minutes. |
| There is abnormal sound of refrigerant flowing when just turning on or turning off the unit | Water-running sound can be heard | Normal phenomenon. Abnormal sound will disappear after a few minutes. |
| There is touching sound of foreign objects or parts inside the unit | The unit gives out abnormal sound | Take out the foreign objects; adjust the position of each part inside the unit; tighten the connection screws; apply some damping gum on the touching parts |
| Abnormal shake of compressor | Outdoor unit gives out abnormal sound | Adjust the support foot mat of compressor, tighten the bolts |
| Abnormal sound inside the compressor | Abnormal sound inside the compressor | If add too much refrigerant during maintenance, please reduce refrigerant properly. Replace compressor for other circumstances. |

40	Maintenance

Service Manual

  - Exploded View and Parts List

DRY PURY 11	DRY PURY 13	DRY PURY 17

The component picture is only for reference; please refer to the actual product.

Maintenance	41

Service Manual

| NO. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  |  | DRY PURY 13 | DRY PURY 17 |  |
|  | Product code |  |  |  |  |
| 1 | Supporting Strip(Front Panel) |  | 200175060034 | 200175060034 | 1 |
| 2 | Front Panel |  | 200003060176 | 200003060176T | 1 |
| 3 | Membrane |  | 600006060168 | 600006060168 | 1 |
| 4 | Front Panel Sub-Assy |  | 209004060128 | 209004060128 | 1 |
| 5 | Partition Pole (PC board) |  | 7671101601 | 7671101601 | 1 |
| 6 | Water Tank |  | 200103060005 | 200103060005 | 1 |
| 7 | Water Tank Cover |  | 200104060006 | 200104060006 | 1 |
| 8 | Buoy (magnet) |  | 812360000001 | 812360000001 | 1 |
| 9 | Water Tank Sub-Assy |  | 000094060006 | 000094060006 | 1 |
| 10 | Baffle Plate |  | 200012060040 | 200012060040 | 1 |
| 11 | Left Side Plate |  | 200239060014 | 200239060014 | 1 |
| 12 | Centrifugal Fan |  | 103003060014 | 103003060014 | 1 |
| 13 | Fan Motor |  | 150101060199 | 15010106019902 | 1 |
| 14 | Air Flue Assy |  | 000011060040 | 000011060112 | 1 |
| 15 | Diversion Circle |  | 200150060008 | 200150060008 | 1 |
| 16 | Temperature Sensor |  | 390000595 | 390000595 | 20KT |
| 17 | Coping |  | 200106060034 | 200106060034 | 1 |
| 18 | Display Board |  | 300001060584 | 300001060584 | 1 |
| 19 | Top Cover Assy |  | 000097060231 | 000097060231 | 1 |
| 20 | Wire Clamp |  | 26116069 | 26116069 | 1 |
| 21 | Condenser Sub-Assy |  | 010002000009P | 010002000009P | 1 |
| 22 | Capillary Sub-assy |  | 030006060487 | 030006060487 | 1 |
| 23 | Evaporator Sub-Assy |  | 010001000008P | 010001000008P | 1 |
| 24 | Heat-exchange Equipment |  | 011004060015 | 011004060015P | 1 |
| 25 | Rear Plate |  | 200245060014 | 200245060014 | 1 |
| 26 | Rear Plate Sub-Assy |  | 209051060004 | 209051060004 | 1 |
| 27 | Latch |  | 70811002 | 70811002 | 2 |
| 28 | Filter Sub-Assy |  | 111001060159 | 111001060159 | 1 |
| 29 | Front Grill |  | 200226060018 | 200226060018 | 1 |
| 30 | Filter Assy |  | 000064060005 | 000064060005 | 1 |
| 31 | Electric Box |  | 012017060277 | 012017060277 | 1 |
| 32 | fixed support (mainboard) |  | 200115060013 | 200115060013 | 1 |
| 33 | Main Board |  | 300002061054 | 300002061054 | 1 |
| 34 | Capacitor CBB61 |  | 3301074716 | 3301074716 | 1 |
| 35 | Electric Box Assy |  | 100002067031 | 100002067031 | 1 |
| 36 | Electric Box Cover |  | 012020060213A | 012020060213A | 1 |
| 37 | Right Side Plate |  | 200239060015 | 200239060015 | 1 |
| 38 | Power Cord |  | 4002028645 | 4002028645 | 1 |
| 39 | Inhalation Tube |  | 035006061054 | 035006062188 | 1 |
| 40 | Fastener |  | 01211500001 | 01211500001 | 4 |
| 41 | Compressor and Fittings |  | 009001060216 | 009001060543 | 1 |
| 42 | Compressor Gasket |  | 76716057 | 76716057 | 4 |
| 43 | Chassis Sub-assy |  | 209020060029 | 209020060029 | 1 |
| 44 | Castor |  | 24236554 | 24236554 | 4 |
| 45 | Rubber Plug |  | 76716059 | 76716059 | 4 |
| 46 | Chassis Assy |  | 209058060229 | 209058060229 | 1 |
| 47 | Detecting Plate |  | 300018060144 | 300018060144 | 1 |
| 48 | Sensor Cover |  | 200156060009 | 200156060009 | 1 |
| 49 | Adaptor sub-assy |  | 26116155 | 26116155 | 1 |
| 50 | Adaptor |  | 26116154 | 26116154 | 1 |
| 51 | Discharge Tube |  | 035008061069 | 035008062244 | 1 |
| 52 | Water Tray 1 |  | 200063060003 | 200063060003 | 1 |
| 53 | Proximity Switch |  | 430015000003 | 430015000003 | 1 |
| 54 | Supporting Strip |  | 200175060020 | 200175060020 | 1 |
| 55 | Water Tray Assy |  | 000069060121 | 000069060121 | 1 |
| 56 | Water Tray Sub-Assy |  | 209041060016 | 209041060016 | 1 |
| 57 | Water Tray 2 |  | 200063060004 | 200063060004 | 1 |
| 58 | Rubber Plug |  | 76716054 | 76716059 | 1 |
| 59 | Cover of drainage hole |  | 2224609703 | 2224609703 | 1 |

Above data is subject to change without notice.

42	Maintenance

Service Manual

| NO. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | DRY PURY 11 |  |  |
|  | Product code |  |  |  |
| 1 | Supporting Strip(Front Panel) | 200175060034 |  | 1 |
| 2 | Front Panel | 200003060176 |  | 1 |
| 3 | Membrane | 600006060168 |  | 1 |
| 4 | Front Panel Sub-Assy | 209004060128 |  | 1 |
| 5 | Partition Pole (PC board) | 7671101601 |  | 1 |
| 6 | Water Tank | 200103060005 |  | 1 |
| 7 | Water Tank Cover | 200104060006 |  | 1 |
| 8 | Buoy (magnet) | 812360000001 |  | 1 |
| 9 | Water Tank Sub-Assy | 000094060006 |  | 1 |
| 10 | Baffle Plate | 200012060040 |  | 1 |
| 11 | Left Side Plate | 200239060014 |  | 1 |
| 12 | Centrifugal Fan | 103003060014 |  | 1 |
| 13 | Fan Motor | 150101060199 |  | 1 |
| 14 | Air Flue Assy | 000011060040 |  | 1 |
| 15 | Diversion Circle | 200150060008 |  | 1 |
| 16 | Temperature Sensor | 390000595 |  | 20KT |
| 17 | Coping | 200106060034 |  | 1 |
| 18 | Display Board | 300001060584 |  | 1 |
| 19 | Top Cover Assy | 000097060231 |  | 1 |
| 20 | Wire Clamp | 26116069 |  | 1 |
| 21 | Condenser Sub-Assy | 01136106P |  | 1 |
| 22 | Capillary Sub-assy | 030006061046 |  | 1 |
| 23 | Evaporator Sub-Assy | 010001060465P |  | 1 |
| 24 | Heat-exchange Equipment | 011004060041P |  | 1 |
| 25 | Rear Plate | 200245060014 |  | 1 |
| 26 | Rear Plate Sub-Assy | 209051060004 |  | 1 |
| 27 | Latch | 70811002 |  | 2 |
| 28 | Filter Sub-Assy | 111001060159 |  | 1 |
| 29 | Front Grill | 200226060018 |  | 1 |
| 30 | Filter Assy | 000064060005 |  | 1 |
| 31 | Electric Box | 012017060277 |  | 1 |
| 32 | fixed support (mainboard) | 200115060013 |  | 1 |
| 33 | Main Board | 300002061054 |  | 1 |
| 34 | Capacitor CBB61 | 3301074716 |  | 1 |
| 35 | Electric Box Assy | 100002067031 |  | 1 |
| 36 | Electric Box Cover | 012020060213A |  | 1 |
| 37 | Right Side Plate | 200239060015 |  | 1 |
| 38 | Power Cord | 4002028637 |  | 1 |
| 39 | Inhalation Tube | 035006062408 |  | 1 |
| 40 | Fastener | 01211500001 |  | 4 |
| 41 | Compressor and Fittings | 009001060614 |  | 1 |
| 42 | Compressor Gasket | 009012060011 |  | 4 |
| 43 | Chassis Sub-assy | 209020060029 |  | 1 |
| 44 | Castor | 24236554 |  | 4 |
| 45 | Rubber Plug | 76716059 |  | 4 |
| 46 | Chassis Assy | 209058060229 |  | 1 |
| 47 | Detecting Plate | 300018060144 |  | 1 |
| 48 | Sensor Cover | 200156060009 |  | 1 |
| 49 | Adaptor sub-assy | 26116155 |  | 1 |
| 50 | Adaptor | 26116154 |  | 1 |
| 51 | Discharge Tube | 035008062483 |  | 1 |
| 52 | Water Tray 1 | 200063060003 |  | 1 |
| 53 | Proximity Switch | 430015000003 |  | 1 |
| 54 | Supporting Strip | 200175060020 |  | 1 |
| 55 | Water Tray Assy | 000069060121 |  | 1 |
| 56 | Water Tray Sub-Assy | 209041060016 |  | 1 |
| 57 | Water Tray 2 | 200063060004 |  | 1 |
| 58 | Rubber Plug | 76716054 |  | 1 |
| 59 | Cover of drainage hole | 2224609703 |  | 1 |

Above data is subject to change without notice.

Maintenance	43

Service Manual

DRY PURY 21

DRY PURY 25

5	6	7	8	9	10   11	12   13   14	15	16   17   18	19	20	21	22	23	24	25	26	27	28	29	30

The component picture is only for reference; please refer to the actual product.

44	Maintenance

Service Manual

| NO. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | DRY PURY 21 | DRY PURY 25 |  |
|  | Product code |  |  |  |
| 1 | Supporting Strip(Front Panel) | 200175060035 | 200175060035 | 1 |
| 2 | Front Panel | 200003060182 | 200003060182 | 1 |
| 3 | Front Panel Sub-Assy | 209004060134 | 209004060134 | 1 |
| 4 | Membrane | 600006060182 | 600006060182 | 1 |
| 5 | Partition Pole (PC board) | 7671101601 | 7671101601 | 1 |
| 6 | Buoy (magnet) | 812360000001 | 812360000001 | 1 |
| 7 | Water Tank | 200103060006 | 200103060006 | 1 |
| 8 | Water Tank Cover | 200104060007 | 200104060007 | 1 |
| 9 | Water Tank Sub-Assy | 000094060007 | 000094060007 | 1 |
| 10 | Baffle Plate | 200012060031 | 200012060031 | 1 |
| 11 | Left Side Plate | 200239060017 | 200239060017 | 1 |
| 12 | Centrifugal Fan | 103003060026 | 103003060026 | 1 |
| 13 | Fan Motor | 1501605709 | 1501605710 | 1 |
| 14 | Air Flue Assy | 000011060097 | 000011060126 | 1 |
| 15 | Diversion Circle | 200150060022 | 200150060022 | 1 |
| 16 | Coping | 200106060041 | 200106060041 | 1 |
| 17 | Display Board | 300001060584 | 300001060584 | 1 |
| 18 | Temperature Sensor | 390000595 | 390000595 | 1 |
| 19 | Wire Clamp | 26116069 | 26116069 | 1 |
| 20 | Top Cover Assy | 000097060258 | 000097060258 | 1 |
| 21 | Condenser Sub-Assy | 010002060236P | 010002060236P | 1 |
| 22 | Capillary Sub-assy | 030006060681 | 030006060681 | 1 |
| 23 | Evaporator Sub-Assy | 010001060323P | 010001060323P | 1 |
| 24 | Heat-exchange Equipment | 011004060026P | 011004060026P | 1 |
| 25 | Rear Plate | 200245060015 | 200245060015 | 1 |
| 26 | Rear Plate Sub-Assy | 209051060005 | 209051060005 | 1 |
| 27 | Latch | 70811002 | 70811002 | 2 |
| 28 | Filter Sub-Assy | 111001060161 | 111001060161 | 1 |
| 29 | Front Grill | 200226060020 | 200226060020 | 1 |
| 30 | Front Grill Assy | 000236060005 | 000236060005 | 1 |
| 31 | Electric Box | 012017060277 | 012017060277 | 1 |
| 32 | fixed support (mainboard) | 200115060013 | 200115060013 | 1 |
| 33 | Main Board | 300002061152 | 300002061152 | 1 |
| 34 | Capacitor CBB61 | 3301074716 | 3301074701 | 1 |
| 35 | Electric Box Assy | 100002067821 | 10000206782102 | 1 |
| 36 | Electric Box Cover | 012020060213A | 012020060213A | 1 |
| 37 | Right Side Plate | 200239060016 | 200239060016 | 1 |
| 38 | Inhalation Tube | 035006061608 | 035006061608 | 1 |
| 39 | Discharge Tube | 035008061657 | 035008061657 | 1 |
| 40 | Power Cord | 4002028636 | 4002028636 | 1 |
| 41 | Detecting Plate | 300018060144 | 300018060144 | 1 |
| 42 | Castor | 24236554 | 24236554 | 4 |
| 43 | Rubber Plug | 76716059 | 76716059 | 4 |
| 44 | Chassis Sub-assy | 209020060030 | 209020060030 | 1 |
| 45 | Chassis Assy | 209058060239 | 209058060239 | 1 |
| 46 | Compressor Gasket | 009012060011 | 009012060011 | 4 |
| 47 | Compressor and Fittings | 009001060419 | 009001060419 | 1 |
| 48 | Joint | 26116154 | 26116154 | 1 |
| 49 | Adaptor sub-assy | 26116155 | 26116155 | 1 |
| 50 | Water Tray 1 | 200063060012 | 200063060012 | 1 |
| 51 | Supporting Strip | 200175060020 | 200175060020 | 1 |
| 52 | Proximity Switch | 430015000003 | 430015000003 | 1 |
| 53 | Rubber Plug | 76716054 | 76716054 | 1 |
| 54 | Cover of drainage hole | 2224609703 | 2224609703 | 1 |
| 55 | Water Tray 2 | 200063060013 | 200063060013 | 1 |
| 56 | Water Tray Assy | 000069060229 | 000069060229 | 1 |

Above data is subject to change without notice.

Maintenance	45

Service Manual

  - Removal Procedure

Warning: disconnect power supply before removal; Prohibit disassembling and maintaining the refrigeration system pipeline and parts (include evaporator, condenser, compressor,capillary, etc.)

| Step | Procedure |
| --- | --- |
| 1. Remove water tank sub-assy | Water tank assembly Hold this position to pull it along the arrow direction |
|  | Hold the hand-holding position at the bottom of the water tank, pull the water tank (along the arrow position) and then remove the water tank sub-assy. |  |
| 2. Remove filter sub-assy | Door switch Press this position with a hand Filter sub-assy |
|  | Press "PUSH" position with a hand to separate it from these 2 door switches on the rear plate, and then remove the filter sub-assy. |  |
| 3. Remove rear plate sub-assy | Clasp Screw Rear plate sub-assy Screw |
|  | Remove 3 screws on the back of the case and 1 screw under the water tank, pull it rear plate sub-assy outwards to separate it from all clasps and then the rear plate sub-assy can be removed. |  |

46	Maintenance

Service Manual

| Step | Procedure |
| --- | --- |
| 4. Remove panel | Clasp Screw Panel |
|  | Remove 2 screws under the water tank, pull the panel outwards to make it come out of all clasps and then remove the panel. |  |
| 5. Remove right side plate | Screw Clasp Right side plate Screw |
|  | Remove 5 screws used for fixing the right side plate and then pull the right side plate outwards to separate it from 4 clasps in the middle, and then the right side plate can be removed. |  |
| 6. Remove left side plate | Screw Clasp Left side plate |
|  | Remove 3 screws used for fixing the left side plate and then pull the left side plate outwards to separate it from 4 clasps in the middle, and then the left side plate can be removed. |  |
| 7. Remove electric box cover | Screw Electric box cover |
|  | Remove 2 screws on the electric box cover and then remove the electric box cover. |  |

Maintenance	47

Service Manual

| Step | Procedure |
| --- | --- |
| 8. Remove top cover sub-assy | Screw Top cover sub-assy Clasp |
|  | Remove 4 screws used for fixing the top cover sub-assy, and take it outwards to separate these 2 clasps in front of the top cover sub-assy. Separate connection wires of discharge temperature sensor and display board to separate from all grooves, hold two sides of the top cover sub-assy, pull it upwards and then remove the top cover sub-assy. |  |
| 9. Remove display sub-assy | Screw Display sbu-assy Top cover |
|  | Remove 4 screws used for fixing the display, separate the display sbu-assy from the clasps and then remove the display sub-assy. |  |
| 10. Remove Baffle Plate | Baffle plate Clasp Clasp Screw |
|  | Remove the screws under the baffle Plate,separate the baffle plate from the clasp and then remoe the baffle plate. |  |

48	Maintenance

Service Manual

| Step | Procedure |
| --- | --- |
| 11. Remove electric box | Electric box Screw |
|  | Pull out all wires connected with all electric elements inside the electric box, remove 2 screws connected with the water tray inside the electric box, and then remove the electric box. |  |
| 12. Remove air duct |  |
|  | Remove 1 screw used for fixing the water tray and 2 screws used for fixing the evaporator and the condenser, pull the air duct backwards and then remove the air duct. |  |
| 13. Remove centrifugal blade |  |
|  | Remove nuts used for fixing the blades at the motor terminal and 2 washer; pull the blade along the motor shaft and then remove the blade sub-assy. |  |

Maintenance	49

Service Manual

| Step | Procedure |
| --- | --- |
| 14. Remove motor |  |
|  | Pull out the wire-pressing plate, remove 3 screws used for fixing the motor and then remove the motor. |  |

50	Maintenance

Service Manual

Appendix:

Appendix 1: Reference Sheet of Celsius and Fahrenheit

Conversion formula for Fahrenheit degree and Celsius degree: Tf=Tcx1.8+32 Set temperature

）

Ambient temperature

）

Maintenance	51

Service Manual

Appendix 2: Resistance Table of Temperature Sensor

Resistance table of ambient temperature sensor (15K)

| Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -2.2 | 138.1 |  | 68 | 18.75 |  | 138.2 | 3.848 |  | 208.4 | 1.071 |
| -0.4 | 128.6 |  | 69.8 | 17.93 |  | 140 | 3.711 |  | 210.2 | 1.039 |
| 1.4 | 121.6 |  | 71.6 | 17.14 |  | 141.8 | 3.579 |  | 212 | 1.009 |
| 3.2 | 115 |  | 73.4 | 16.39 |  | 143.6 | 3.454 |  | 213.8 | 0.98 |
| 5 | 108.7 |  | 75.2 | 15.68 |  | 145.4 | 3.333 |  | 215.6 | 0.952 |
| 6.8 | 102.9 |  | 77 | 15 |  | 147.2 | 3.217 |  | 217.4 | 0.925 |
| 8.6 | 97.4 |  | 78.8 | 14.36 |  | 149 | 3.105 |  | 219.2 | 0.898 |
| 10.4 | 92.22 |  | 80.6 | 13.74 |  | 150.8 | 2.998 |  | 221 | 0.873 |
| 12.2 | 87.35 |  | 82.4 | 13.16 |  | 152.6 | 2.896 |  | 222.8 | 0.848 |
| 14 | 82.75 |  | 84.2 | 12.6 |  | 154.4 | 2.797 |  | 224.6 | 0.825 |
| 15.8 | 78.43 |  | 86 | 12.07 |  | 156.2 | 2.702 |  | 226.4 | 0.802 |
| 17.6 | 74.35 |  | 87.8 | 11.57 |  | 158 | 2.611 |  | 228.2 | 0.779 |
| 19.4 | 70.5 |  | 89.6 | 11.09 |  | 159.8 | 2.523 |  | 230 | 0.758 |
| 21.2 | 66.88 |  | 91.4 | 10.63 |  | 161.6 | 2.439 |  | 231.8 | 0.737 |
| 23 | 63.46 |  | 93.2 | 10.2 |  | 163.4 | 2.358 |  | 233.6 | 0.717 |
| 24.8 | 60.23 |  | 95 | 9.779 |  | 165.2 | 2.28 |  | 235.4 | 0.697 |
| 26.6 | 57.18 |  | 96.8 | 9.382 |  | 167 | 2.206 |  | 237.2 | 0.678 |
| 28.4 | 54.31 |  | 98.6 | 9.003 |  | 168.8 | 2.133 |  | 239 | 0.66 |
| 30.2 | 51.59 |  | 100.4 | 8.642 |  | 170.6 | 2.064 |  | 240.8 | 0.642 |
| 32 | 49.02 |  | 102.2 | 8.297 |  | 172.4 | 1.997 |  | 242.6 | 0.625 |
| 33.8 | 46.6 |  | 104 | 7.967 |  | 174.2 | 1.933 |  | 244.4 | 0.608 |
| 35.6 | 44.31 |  | 105.8 | 7.653 |  | 176 | 1.871 |  | 246.2 | 0.592 |
| 37.4 | 42.14 |  | 107.6 | 7.352 |  | 177.8 | 1.811 |  | 248 | 0.577 |
| 39.2 | 40.09 |  | 109.4 | 7.065 |  | 179.6 | 1.754 |  | 249.8 | 0.561 |
| 41 | 38.15 |  | 111.2 | 6.791 |  | 181.4 | 1.699 |  | 251.6 | 0.547 |
| 42.8 | 36.32 |  | 113 | 6.529 |  | 183.2 | 1.645 |  | 253.4 | 0.532 |
| 44.6 | 34.58 |  | 114.8 | 6.278 |  | 185 | 1.594 |  | 255.2 | 0.519 |
| 46.4 | 32.94 |  | 116.6 | 6.038 |  | 186.8 | 1.544 |  | 257 | 0.505 |
| 48.2 | 31.38 |  | 118.4 | 5.809 |  | 188.6 | 1.497 |  | 258.8 | 0.492 |
| 50 | 29.9 |  | 120.2 | 5.589 |  | 190.4 | 1.451 |  | 260.6 | 0.48 |
| 51.8 | 28.51 |  | 122 | 5.379 |  | 192.2 | 1.408 |  | 262.4 | 0.467 |
| 53.6 | 27.18 |  | 123.8 | 5.197 |  | 194 | 1.363 |  | 264.2 | 0.456 |
| 55.4 | 25.92 |  | 125.6 | 4.986 |  | 195.8 | 1.322 |  | 266 | 0.444 |
| 57.2 | 24.73 |  | 127.4 | 4.802 |  | 197.6 | 1.282 |  | 267.8 | 0.433 |
| 59 | 23.6 |  | 129.2 | 4.625 |  | 199.4 | 1.244 |  | 269.6 | 0.422 |
| 60.8 | 22.53 |  | 131 | 4.456 |  | 201.2 | 1.207 |  | 271.4 | 0.412 |
| 62.6 | 21.51 |  | 132.8 | 4.294 |  | 203 | 1.171 |  | 273.2 | 0.401 |
| 64.4 | 20.54 |  | 134.6 | 4.139 |  | 204.8 | 1.136 |  | 275 | 0.391 |
| 66.2 | 19.63 |  | 136.4 | 3.99 |  | 206.6 | 1.103 |  | 276.8 | 0.382 |

52	Maintenance

Service Manual

Resistance Table of Tube Temperature Sensors (20K)

| Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -2.2 | 181.4 |  | 68 | 25.01 |  | 138.2 | 5.13 |  | 208.4 | 1.427 |
| -0.4 | 171.4 |  | 69.8 | 23.9 |  | 140 | 4.948 |  | 210.2 | 1.386 |
| 1.4 | 162.1 |  | 71.6 | 22.85 |  | 141.8 | 4.773 |  | 212 | 1.346 |
| 3.2 | 153.3 |  | 73.4 | 21.85 |  | 143.6 | 4.605 |  | 213.8 | 1.307 |
| 5 | 145 |  | 75.2 | 20.9 |  | 145.4 | 4.443 |  | 215.6 | 1.269 |
| 6.8 | 137.2 |  | 77 | 20 |  | 147.2 | 4.289 |  | 217.4 | 1.233 |
| 8.6 | 129.9 |  | 78.8 | 19.14 |  | 149 | 4.14 |  | 219.2 | 1.198 |
| 10.4 | 123 |  | 80.6 | 18.13 |  | 150.8 | 3.998 |  | 221 | 1.164 |
| 12.2 | 116.5 |  | 82.4 | 17.55 |  | 152.6 | 3.861 |  | 222.8 | 1.131 |
| 14 | 110.3 |  | 84.2 | 16.8 |  | 154.4 | 3.729 |  | 224.6 | 1.099 |
| 15.8 | 104.6 |  | 86 | 16.1 |  | 156.2 | 3.603 |  | 226.4 | 1.069 |
| 17.6 | 99.13 |  | 87.8 | 15.43 |  | 158 | 3.481 |  | 228.2 | 1.039 |
| 19.4 | 94 |  | 89.6 | 14.79 |  | 159.8 | 3.364 |  | 230 | 1.01 |
| 21.2 | 89.17 |  | 91.4 | 14.18 |  | 161.6 | 3.252 |  | 231.8 | 0.983 |
| 23 | 84.61 |  | 93.2 | 13.59 |  | 163.4 | 3.144 |  | 233.6 | 0.956 |
| 24.8 | 80.31 |  | 95 | 13.04 |  | 165.2 | 3.04 |  | 235.4 | 0.93 |
| 26.6 | 76.24 |  | 96.8 | 12.51 |  | 167 | 2.94 |  | 237.2 | 0.904 |
| 28.4 | 72.41 |  | 98.6 | 12 |  | 168.8 | 2.844 |  | 239 | 0.88 |
| 30.2 | 68.79 |  | 100.4 | 11.52 |  | 170.6 | 2.752 |  | 240.8 | 0.856 |
| 32 | 65.37 |  | 102.2 | 11.06 |  | 172.4 | 2.663 |  | 242.6 | 0.833 |
| 33.8 | 62.13 |  | 104 | 10.62 |  | 174.2 | 2.577 |  | 244.4 | 0.811 |
| 35.6 | 59.08 |  | 105.8 | 10.2 |  | 176 | 2.495 |  | 246.2 | 0.77 |
| 37.4 | 56.19 |  | 107.6 | 9.803 |  | 177.8 | 2.415 |  | 248 | 0.769 |
| 39.2 | 53.46 |  | 109.4 | 9.42 |  | 179.6 | 2.339 |  | 249.8 | 0.746 |
| 41 | 50.87 |  | 111.2 | 9.054 |  | 181.4 | 2.265 |  | 251.6 | 0.729 |
| 42.8 | 48.42 |  | 113 | 8.705 |  | 183.2 | 2.194 |  | 253.4 | 0.71 |
| 44.6 | 46.11 |  | 114.8 | 8.37 |  | 185 | 2.125 |  | 255.2 | 0.692 |
| 46.4 | 43.92 |  | 116.6 | 8.051 |  | 186.8 | 2.059 |  | 257 | 0.674 |
| 48.2 | 41.84 |  | 118.4 | 7.745 |  | 188.6 | 1.996 |  | 258.8 | 0.658 |
| 50 | 39.87 |  | 120.2 | 7.453 |  | 190.4 | 1.934 |  | 260.6 | 0.64 |
| 51.8 | 38.01 |  | 122 | 7.173 |  | 192.2 | 1.875 |  | 262.4 | 0.623 |
| 53.6 | 36.24 |  | 123.8 | 6.905 |  | 194 | 1.818 |  | 264.2 | 0.607 |
| 55.4 | 34.57 |  | 125.6 | 6.648 |  | 195.8 | 1.736 |  | 266 | 0.592 |
| 57.2 | 32.98 |  | 127.4 | 6.403 |  | 197.6 | 1.71 |  | 267.8 | 0.577 |
| 59 | 31.47 |  | 129.2 | 6.167 |  | 199.4 | 1.658 |  | 269.6 | 0.563 |
| 60.8 | 30.04 |  | 131 | 5.942 |  | 201.2 | 1.609 |  | 271.4 | 0.549 |
| 62.6 | 28.68 |  | 132.8 | 5.726 |  | 203 | 1.561 |  | 273.2 | 0.535 |
| 64.4 | 27.39 |  | 134.6 | 5.519 |  | 204.8 | 1.515 |  | 275 | 0.521 |
| 66.2 | 26.17 |  | 136.4 | 5.32 |  | 206.6 | 1.47 |  | 276.8 | 0.509 |

Maintenance	53

Service Manual

Resistance Table of Discharge Temperature Sensor (50K)

| Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |  | Temp.(oF) | Resistance(kΩ) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -20.2 | 853.5 |  | 50 | 98 |  | 120.2 | 18.34 |  | 190.4 | 4.754 |
| -18.4 | 799.8 |  | 51.8 | 93.42 |  | 122 | 17.65 |  | 192.2 | 4.609 |
| -16.6 | 750 |  | 53.6 | 89.07 |  | 123.8 | 16.99 |  | 194 | 4.469 |
| -14.8 | 703.8 |  | 55.4 | 84.95 |  | 125.6 | 16.36 |  | 195.8 | 4.334 |
| -13 | 660.8 |  | 57.2 | 81.05 |  | 127.4 | 15.75 |  | 197.6 | 4.204 |
| -11.2 | 620.8 |  | 59 | 77.35 |  | 129.2 | 15.17 |  | 199.4 | 4.079 |
| -9.4 | 580.6 |  | 60.8 | 73.83 |  | 131 | 14.62 |  | 201.2 | 3.958 |
| -7.6 | 548.9 |  | 62.6 | 70.5 |  | 132.8 | 14.09 |  | 203 | 3.841 |
| -5.8 | 516.6 |  | 64.4 | 67.34 |  | 134.6 | 13.58 |  | 204.8 | 3.728 |
| -4 | 486.5 |  | 66.2 | 64.33 |  | 136.4 | 13.09 |  | 206.6 | 3.619 |
| -2.2 | 458.3 |  | 68 | 61.48 |  | 138.2 | 12.62 |  | 208.4 | 3.514 |
| -0.4 | 432 |  | 69.8 | 58.77 |  | 140 | 12.17 |  | 210.2 | 3.413 |
| 1.4 | 407.4 |  | 71.6 | 56.19 |  | 141.8 | 11.74 |  | 212 | 3.315 |
| 3.2 | 384.5 |  | 73.4 | 53.74 |  | 143.6 | 11.32 |  | 213.8 | 3.22 |
| 5 | 362.9 |  | 75.2 | 51.41 |  | 145.4 | 10.93 |  | 215.6 | 3.129 |
| 6.8 | 342.8 |  | 77 | 49.19 |  | 147.2 | 10.54 |  | 217.4 | 3.04 |
| 8.6 | 323.9 |  | 78.8 | 47.08 |  | 149 | 10.18 |  | 219.2 | 2.955 |
| 10.4 | 306.2 |  | 80.6 | 45.07 |  | 150.8 | 9.827 |  | 221 | 2.872 |
| 12.2 | 289.6 |  | 82.4 | 43.16 |  | 152.6 | 9.489 |  | 222.8 | 2.792 |
| 14 | 274 |  | 84.2 | 41.34 |  | 154.4 | 9.165 |  | 224.6 | 2.715 |
| 15.8 | 259.3 |  | 86 | 39.61 |  | 156.2 | 8.854 |  | 226.4 | 2.64 |
| 17.6 | 245.6 |  | 87.8 | 37.96 |  | 158 | 8.555 |  | 228.2 | 2.568 |
| 19.4 | 232.6 |  | 89.6 | 36.38 |  | 159.8 | 8.268 |  | 230 | 2.498 |
| 21.2 | 220.5 |  | 91.4 | 34.88 |  | 161.6 | 7.991 |  | 231.8 | 2.431 |
| 23 | 209 |  | 93.2 | 33.45 |  | 163.4 | 7.726 |  | 233.6 | 2.365 |
| 24.8 | 198.3 |  | 95 | 32.09 |  | 165.2 | 7.47 |  | 235.4 | 2.302 |
| 26.6 | 199.1 |  | 96.8 | 30.79 |  | 167 | 7.224 |  | 237.2 | 2.241 |
| 28.4 | 178.5 |  | 98.6 | 29.54 |  | 168.8 | 6.998 |  | 239 | 2.182 |
| 30.2 | 169.5 |  | 100.4 | 28.36 |  | 170.6 | 6.761 |  | 240.8 | 2.124 |
| 32 | 161 |  | 102.2 | 27.23 |  | 172.4 | 6.542 |  | 242.6 | 2.069 |
| 33.8 | 153 |  | 104 | 26.15 |  | 174.2 | 6.331 |  | 244.4 | 2.015 |
| 35.6 | 145.4 |  | 105.8 | 25.11 |  | 176 | 6.129 |  | 246.2 | 1.963 |
| 37.4 | 138.3 |  | 107.6 | 24.13 |  | 177.8 | 5.933 |  | 248 | 1.912 |
| 39.2 | 131.5 |  | 109.4 | 23.19 |  | 179.6 | 5.746 |  | 249.8 | 1.863 |
| 41 | 125.1 |  | 111.2 | 22.29 |  | 181.4 | 5.565 |  | 251.6 | 1.816 |
| 42.8 | 119.1 |  | 113 | 21.43 |  | 183.2 | 5.39 |  | 253.4 | 1.77 |
| 44.6 | 113.4 |  | 114.8 | 20.6 |  | 185 | 5.222 |  | 255.2 | 1.725 |
| 46.4 | 108 |  | 116.6 | 19.81 |  | 186.8 | 5.06 |  | 257 | 1.682 |
| 48.2 | 102.8 |  | 118.4 | 19.06 |  | 188.6 | 4.904 |  | 258.8 | 1.64 |

54	Maintenance

Service Manual

Resistance table of ambient temperature sensor (100K)

| Temp(oF) | Resistance(kΩ) |  | Temp(oF) | Resistance(kΩ) |  | Temp(oF) | Resistance(kΩ) |  | Temp(oF) | Resistance(kΩ) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -4.0 | 925.998 |  | 64.4 | 136.845 |  | 132.8 | 28.638 |  | 201.2 | 7.918 |
| -2.2 | 876.141 |  | 66.2 | 130.752 |  | 134.6 | 27.600 |  | 203.0 | 7.676 |
| -0.4 | 829.261 |  | 68.0 | 124.961 |  | 136.4 | 26.606 |  | 204.8 | 7.443 |
| 1.4 | 785.155 |  | 69.8 | 119.456 |  | 138.2 | 25.652 |  | 206.6 | 7.218 |
| 3.2 | 743.636 |  | 71.6 | 114.221 |  | 140.0 | 24.737 |  | 208.4 | 7.000 |
| 5.0 | 704.532 |  | 73.4 | 109.242 |  | 141.8 | 23.858 |  | 210.2 | 6.790 |
| 6.8 | 667.688 |  | 75.2 | 104.506 |  | 143.6 | 23.016 |  | 212.0 | 6.587 |
| 8.6 | 632.956 |  | 77.0 | 100.000 |  | 145.4 | 22.207 |  | 213.8 | 6.391 |
| 10.4 | 600.201 |  | 78.8 | 95.711 |  | 147.2 | 21.430 |  | 215.6 | 6.201 |
| 12.2 | 569.300 |  | 80.6 | 91.629 |  | 149.0 | 20.684 |  | 217.4 | 6.018 |
| 14.0 | 540.135 |  | 82.4 | 87.742 |  | 150.8 | 19.697 |  | 219.2 | 5.842 |
| 15.8 | 512.601 |  | 84.2 | 84.041 |  | 152.6 | 19.279 |  | 221.0 | 5.671 |
| 17.6 | 486.596 |  | 86.0 | 80.515 |  | 154.4 | 18.617 |  | 222.8 | 5.505 |
| 19.4 | 462.029 |  | 87.8 | 77.155 |  | 156.2 | 17.981 |  | 224.6 | 5.346 |
| 21.2 | 438.812 |  | 89.6 | 73.954 |  | 158.0 | 17.370 |  | 226.4 | 5.191 |
| 23.0 | 416.865 |  | 91.4 | 70.902 |  | 159.8 | 16.782 |  | 228.2 | 5.042 |
| 24.8 | 396.114 |  | 93.2 | 67.993 |  | 161.6 | 16.217 |  | 230.0 | 4.898 |
| 26.6 | 376.487 |  | 95.0 | 65.218 |  | 163.4 | 15.673 |  | 231.8 | 4.758 |
| 28.4 | 357.918 |  | 96.8 | 62.572 |  | 165.2 | 15.150 |  | 233.6 | 4.624 |
| 30.2 | 340.348 |  | 98.6 | 60.017 |  | 167.0 | 14.646 |  | 235.4 | 4.493 |
| 32.0 | 323.717 |  | 100.4 | 57.637 |  | 168.8 | 14.141 |  | 237.2 | 4.367 |
| 33.8 | 307.972 |  | 102.2 | 55.337 |  | 170.6 | 13.695 |  | 239.0 | 4.245 |
| 35.6 | 293.062 |  | 104.0 | 53.141 |  | 172.4 | 13.245 |  | 240.8 | 4.127 |
| 37.4 | 278.941 |  | 105.8 | 51.043 |  | 174.2 | 12.813 |  | 242.6 | 4.012 |
| 39.2 | 265.562 |  | 107.6 | 49.040 |  | 176.0 | 12.396 |  | 244.4 | 3.902 |
| 41.0 | 252.886 |  | 109.4 | 47.126 |  | 177.8 | 11.995 |  | 246.2 | 3.795 |
| 42.8 | 240.871 |  | 111.2 | 45.296 |  | 179.6 | 11.608 |  | 248.0 | 3.691 |
| 44.6 | 229.482 |  | 113.0 | 43.548 |  | 181.4 | 11.235 |  | 249.8 | 3.591 |
| 46.4 | 218.684 |  | 114.8 | 41.876 |  | 183.2 | 10.876 |  | 251.6 | 3.494 |
| 48.2 | 208.443 |  | 116.6 | 40.276 |  | 185.0 | 10.530 |  | 253.4 | 3.400 |
| 50.0 | 198.729 |  | 118.4 | 38.747 |  | 186.8 | 10.196 |  | 255.2 | 3.309 |
| 51.8 | 189.514 |  | 120.2 | 37.283 |  | 188.6 | 9.874 |  | 257.0 | 3.221 |
| 53.6 | 180.769 |  | 122.0 | 35.882 |  | 190.4 | 9.564 |  | 258.8 | 3.136 |
| 55.4 | 172.469 |  | 123.8 | 34.541 |  | 192.2 | 9.265 |  | 260.6 | 3.053 |
| 57.2 | 164.590 |  | 125.6 | 33.257 |  | 194.0 | 8.976 |  | 262.4 | 2.973 |
| 59.0 | 157.109 |  | 127.4 | 32.027 |  | 195.8 | 8.697 |  | 264.2 | 2.896 |
| 60.8 | 150.005 |  | 129.2 | 30.849 |  | 197.6 | 8.428 |  | 266.0 | 2.821 |
| 62.6 | 143.256 |  | 131.0 | 29.720 |  | 199.4 | 8.169 |  | 267.8 | 2.748 |

Maintenance	55

Service Manual

| Temp(oF) | Resistance(kΩ) |  | Temp(oF) | Resistance(kΩ) |  | Temp(oF) | Resistance(kΩ) |  | Temp(oF) | Resistance(kΩ) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 269.6 | 2.678 |  | 323.6 | 1.312 |  | 377.6 | 0.705 |  | 431.6 | 0.384 |
| 271.4 | 2.610 |  | 325.4 | 1.284 |  | 379.4 | 0.691 |  | 433.4 | 0.376 |
| 273.2 | 2.543 |  | 327.2 | 1.256 |  | 381.2 | 0.677 |  | 435.2 | 0.369 |
| 275.0 | 2.479 |  | 329.0 | 1.229 |  | 383.0 | 0.664 |  | 437.0 | 0.362 |
| 276.8 | 2.417 |  | 330.8 | 1.203 |  | 384.8 | 0.650 |  | 438.8 | 0.355 |
| 278.6 | 2.357 |  | 332.6 | 1.178 |  | 386.6 | 0.637 |  | 440.6 | 0.348 |
| 280.4 | 2.229 |  | 334.4 | 1.153 |  | 388.4 | 0.625 |  | 442.4 | 0.341 |
| 282.2 | 2.242 |  | 336.2 | 1.129 |  | 390.2 | 0.612 |  | 444.2 | 0.335 |
| 284.0 | 2.187 |  | 380.0 | 1.105 |  | 392.0 | 0.600 |  | 446.0 | 0.328 |
| 285.8 | 2.134 |  | 339.8 | 1.082 |  | 393.8 | 0.588 |  | 447.8 | 0.322 |
| 287.6 | 2.082 |  | 341.6 | 1.060 |  | 395.6 | 0.576 |  | 449.6 | 0.317 |
| 289.4 | 2.032 |  | 343.4 | 1.038 |  | 397.4 | 0.565 |  | 451.4 | 0.311 |
| 291.2 | 1.983 |  | 345.2 | 1.017 |  | 399.2 | 0.553 |  | 453.2 | 0.305 |
| 293.0 | 1.936 |  | 347.0 | 0.996 |  | 401.0 | 0.542 |  | 455.0 | 0.300 |
| 294.8 | 1.890 |  | 348.8 | 0.975 |  | 402.8 | 0.531 |  | 456.8 | 0.295 |
| 296.6 | 1.846 |  | 350.6 | 0.956 |  | 404.6 | 0.521 |  | 458.6 | 0.290 |
| 298.4 | 1.803 |  | 352.4 | 0.936 |  | 406.4 | 0.510 |  | 460.4 | 0.285 |
| 300.2 | 1.761 |  | 354.2 | 0.917 |  | 408.2 | 0.500 |  | 462.2 | 0.281 |
| 302.0 | 1.720 |  | 356.0 | 0.899 |  | 410.0 | 0.490 |  | 464.0 | 0.276 |
| 303.8 | 1.680 |  | 357.8 | 0.881 |  | 411.8 | 0.480 |  | 465.8 | 0.272 |
| 305.6 | 1.642 |  | 359.6 | 0.863 |  | 413.6 | 0.470 |  | 467.6 | 0.269 |
| 307.4 | 1.605 |  | 361.4 | 0.845 |  | 415.4 | 0.461 |  | 469.4 | 0.265 |
| 309.2 | 1.568 |  | 363.2 | 0.828 |  | 417.2 | 0.451 |  | 471.2 | 0.261 |
| 311.0 | 1.533 |  | 365.0 | 0.812 |  | 419.0 | 0.442 |  | 473.0 | 0.258 |
| 312.8 | 1.499 |  | 366.8 | 0.796 |  | 420.8 | 0.433 |  | 474.8 | 0.255 |
| 314.6 | 1.466 |  | 368.6 | 0.780 |  | 422.6 | 0.425 |  | 476.6 | 0.253 |
| 316.4 | 1.433 |  | 370.4 | 0.764 |  | 424.4 | 0.416 |  | 478.4 | 0.250 |
| 318.2 | 1.402 |  | 372.2 | 0.749 |  | 426.2 | 0.408 |  | 480.2 | 0.248 |
| 320.0 | 1.371 |  | 374.0 | 0.734 |  | 428.0 | 0.400 |  | 482.0 | 0.246 |
| 321.8 | 1.341 |  | 375.8 | 0.719 |  | 429.8 | 0.392 |  | / | / |

56	Maintenance

Service Manual

Appendix 3: Resistance Value Table of Humidity Sensor

HIS-06 temperature and humidity characteristic5℃～ 14℃	Unit:KΩ

| Relative humidity | Temperature（℃） |
| --- | --- |
| %RH | 5℃ | 6℃ | 7℃ | 8℃ | 9℃ | 10℃ | 11℃ | 12℃ | 13℃ | 14℃ |
| 90 | 5.35 | 4.92 | 4.55 | 4.23 | 3.95 | 3.70 | 3.47 | 3.25 | 3.05 | 2.87 |
| 89 | 5.80 | 5.33 | 4.93 | 4.58 | 4.27 | 4.00 | 3.74 | 3.51 | 3.29 | 3.09 |
| 88 | 6.29 | 5.77 | 5.33 | 4.95 | 4.62 | 4.32 | 4.03 | 3.78 | 3.54 | 3.32 |
| 87 | 6.82 | 6.25 | 5.77 | 5.36 | 4.99 | 4.66 | 4.35 | 4.08 | 3.82 | 3.58 |
| 86 | 7.40 | 6.78 | 6.25 | 5.80 | 5.40 | 5.04 | 4.70 | 4.40 | 4.11 | 3.85 |
| 85 | 8.03 | 7.35 | 6.78 | 6.28 | 5.84 | 5.45 | 5.09 | 4.75 | 4.45 | 4.16 |
| 84 | 8.71 | 7.97 | 7.35 | 6.81 | 6.33 | 5.91 | 5.50 | 5.14 | 4.80 | 4.49 |
| 83 | 9.44 | 8.65 | 7.97 | 7.39 | 6.87 | 6.41 | 5.96 | 5.56 | 5.19 | 4.84 |
| 82 | 10.25 | 9.39 | 8.65 | 8.02 | 7.46 | 6.96 | 6.47 | 6.03 | 5.62 | 5.24 |
| 81 | 11.13 | 10.19 | 9.40 | 8.71 | 8.10 | 7.56 | 7.03 | 6.54 | 6.09 | 5.68 |
| 80 | 12.09 | 11.07 | 10.21 | 9.46 | 8.80 | 8.21 | 7.62 | 7.08 | 6.59 | 6.13 |
| 79 | 13.14 | 12.03 | 11.09 | 10.28 | 9.57 | 8.93 | 8.28 | 7.70 | 7.16 | 6.66 |
| 78 | 14.27 | 13.07 | 12.05 | 11.17 | 10.40 | 9.70 | 8.99 | 8.35 | 7.75 | 7.20 |
| 77 | 15.50 | 14.20 | 13.10 | 12.14 | 11.30 | 10.55 | 9.78 | 9.07 | 8.43 | 7.83 |
| 76 | 16.84 | 15.43 | 14.24 | 13.21 | 12.30 | 11.48 | 10.64 | 9.87 | 9.16 | 8.51 |
| 75 | 18.31 | 16.78 | 15.49 | 14.37 | 13.38 | 12.50 | 11.58 | 10.75 | 9.98 | 9.26 |
| 74 | 19.91 | 18.25 | 16.85 | 15.64 | 14.57 | 13.62 | 12.62 | 11.72 | 10.89 | 10.12 |
| 73 | 21.67 | 19.87 | 18.35 | 17.04 | 15.88 | 14.84 | 13.71 | 12.67 | 11.72 | 10.84 |
| 72 | 23.61 | 21.66 | 20.00 | 18.57 | 17.31 | 16.18 | 14.98 | 13.90 | 12.89 | 11.96 |
| 71 | 25.78 | 23.64 | 21.84 | 20.27 | 18.89 | 17.66 | 16.35 | 15.16 | 14.06 | 13.05 |
| 70 | 28.15 | 25.82 | 23.85 | 22.15 | 20.65 | 19.30 | 17.91 | 16.63 | 15.46 | 14.37 |
| 69 | 30.78 | 28.24 | 26.10 | 24.24 | 22.60 | 21.13 | 19.60 | 18.19 | 16.91 | 15.71 |
| 68 | 33.69 | 30.92 | 28.58 | 26.55 | 24.76 | 23.16 | 21.48 | 19.94 | 18.53 | 17.22 |
| 67 | 36.90 | 33.88 | 31.33 | 29.11 | 27.16 | 25.42 | 23.56 | 21.86 | 20.29 | 18.85 |
| 66 | 40.45 | 37.16 | 34.37 | 31.96 | 29.84 | 27.93 | 25.83 | 23.92 | 22.15 | 20.52 |
| 65 | 44.38 | 40.78 | 37.74 | 35.11 | 32.78 | 30.70 | 28.42 | 26.34 | 24.42 | 22.65 |
| 64 | 48.75 | 44.81 | 41.48 | 38.59 | 36.05 | 33.77 | 31.24 | 28.93 | 26.80 | 24.83 |
| 63 | 53.64 | 49.31 | 45.65 | 42.48 | 39.68 | 37.17 | 34.34 | 31.74 | 29.36 | 27.15 |
| 62 | 59.14 | 54.36 | 50.32 | 46.82 | 43.73 | 40.97 | 37.83 | 34.96 | 32.32 | 29.87 |
| 61 | 65.31 | 60.02 | 55.55 | 51.68 | 48.26 | 45.20 | 41.70 | 38.51 | 35.58 | 32.86 |
| 60 | 72.27 | 66.40 | 61.43 | 57.13 | 53.33 | 49.94 | 46.07 | 42.53 | 39.28 | 36.27 |
| 59 | 80.13 | 73.58 | 68.04 | 63.25 | 59.01 | 55.23 | 50.94 | 47.03 | 43.43 | 40.10 |
| 58 | 88.92 | 81.61 | 75.43 | 70.08 | 65.36 | 61.14 | 56.40 | 52.08 | 48.11 | 44.43 |
| 57 | 98.86 | 90.68 | 83.77 | 77.78 | 72.50 | 67.78 | 62.49 | 57.67 | 53.23 | 49.12 |
| 56 | 112.59 | 102.79 | 94.50 | 87.33 | 81.00 | 75.33 | 69.42 | 64.03 | 59.07 | 54.48 |
| 55 | 122.69 | 112.51 | 103.91 | 96.45 | 89.88 | 84.00 | 77.42 | 71.41 | 65.88 | 60.76 |
| 54 | 137.09 | 125.76 | 116.19 | 107.89 | 100.57 | 94.03 | 86.69 | 79.99 | 73.82 | 68.11 |
| 53 | 153.46 | 140.88 | 130.25 | 121.03 | 112.91 | 105.64 | 97.26 | 89.61 | 82.58 | 76.06 |
| 52 | 172.19 | 158.19 | 146.35 | 136.10 | 127.05 | 118.96 | 109.52 | 100.90 | 92.97 | 85.63 |
| 51 | 193.69 | 178.04 | 164.81 | 153.36 | 143.25 | 134.21 | 123.35 | 113.43 | 104.31 | 95.86 |
| 50 | 218.48 | 200.85 | 185.94 | 173.02 | 161.63 | 151.44 | 139.14 | 127.90 | 117.57 | 108.01 |
| 49 | 247.23 | 227.16 | 210.19 | 195.49 | 182.52 | 170.92 | 156.84 | 143.98 | 132.15 | 121.20 |
| 48 | 278.74 | 256.20 | 237.15 | 220.64 | 206.08 | 193.06 | 177.34 | 163.00 | 149.80 | 137.58 |
| 47 | 315.50 | 289.95 | 268.35 | 249.64 | 233.14 | 218.37 | 200.56 | 184.30 | 169.34 | 155.49 |
| 46 | 357.93 | 328.94 | 304.43 | 283.20 | 264.47 | 247.72 | 227.57 | 209.18 | 192.25 | 176.59 |
| 45 | 406.44 | 373.72 | 346.05 | 322.08 | 300.94 | 282.03 | 259.22 | 238.40 | 219.24 | 201.51 |
| 44 | 463.66 | 426.44 | 394.96 | 367.70 | 343.66 | 322.14 | 296.25 | 272.62 | 250.87 | 230.74 |
| 43 | 531.25 | 488.59 | 452.53 | 421.28 | 393.73 | 369.08 | 339.44 | 312.38 | 287.50 | 264.45 |
| 42 | 611.22 | 562.01 | 520.40 | 484.35 | 452.55 | 424.11 | 390.24 | 359.31 | 330.86 | 304.52 |
| 41 | 707.78 | 650.29 | 601.68 | 559.58 | 522.44 | 489.21 | 450.38 | 414.92 | 382.31 | 352.11 |
| 40 | 823.98 | 756.22 | 698.93 | 649.30 | 605.53 | 566.37 | 521.46 | 480.46 | 442.74 | 407.81 |
| 39 | 962.72 | 882.62 | 814.90 | 756.23 | 704.48 | 658.19 | 604.79 | 556.03 | 511.18 | 469.66 |

Maintenance	57

Service Manual

HIS-06 temperature and humidity characteristic 15℃ ~24℃

Unit:KΩ

| Relative humidity | Temperature（℃） |
| --- | --- |
| %RH | 15℃ | 16℃ | 17℃ | 18℃ | 19℃ | 20℃ | 21℃ | 22℃ | 23℃ | 24℃ |
| 90 | 2.70 | 2.56 | 2.43 | 2.31 | 2.19 | 2.08 | 1.99 | 1.91 | 1.83 | 1.75 |
| 89 | 2.91 | 2.76 | 2.61 | 2.48 | 2.35 | 2.23 | 2.13 | 2.04 | 1.95 | 1.86 |
| 88 | 3.12 | 2.96 | 2.80 | 2.66 | 2.52 | 2.39 | 2.28 | 2.18 | 2.08 | 1.98 |
| 87 | 3.36 | 3.18 | 3.01 | 2.85 | 2.70 | 2.56 | 2.44 | 2.33 | 2.22 | 2.12 |
| 86 | 3.61 | 3.42 | 3.23 | 3.06 | 2.90 | 2.75 | 2.62 | 2.50 | 2.38 | 2.27 |
| 85 | 3.90 | 3.69 | 3.49 | 3.30 | 3.12 | 2.95 | 2.81 | 2.67 | 2.54 | 2.42 |
| 84 | 4.20 | 3.97 | 3.76 | 3.55 | 3.36 | 3.18 | 3.03 | 2.88 | 2.74 | 2.61 |
| 83 | 4.52 | 4.28 | 4.05 | 3.83 | 3.63 | 3.43 | 3.26 | 3.10 | 2.94 | 2.79 |
| 82 | 4.89 | 4.63 | 4.38 | 4.14 | 3.92 | 3.71 | 3.52 | 3.33 | 3.16 | 2.99 |
| 81 | 5.29 | 5.00 | 4.73 | 4.48 | 4.24 | 4.01 | 3.80 | 3.60 | 3.42 | 3.23 |
| 80 | 5.70 | 5.39 | 5.10 | 4.83 | 4.57 | 4.33 | 4.10 | 3.88 | 3.68 | 3.48 |
| 79 | 6.19 | 5.85 | 5.53 | 5.22 | 4.94 | 4.67 | 4.41 | 4.17 | 3.94 | 3.72 |
| 78 | 6.69 | 6.32 | 5.96 | 5.63 | 5.32 | 5.02 | 4.75 | 4.49 | 4.24 | 4.01 |
| 77 | 7.27 | 6.85 | 6.46 | 6.09 | 5.74 | 5.41 | 5.11 | 4.83 | 4.56 | 4.31 |
| 76 | 7.90 | 7.44 | 7.00 | 6.59 | 6.20 | 5.83 | 5.51 | 5.21 | 4.92 | 4.65 |
| 75 | 8.60 | 8.08 | 7.60 | 7.14 | 6.71 | 6.30 | 5.95 | 5.62 | 5.30 | 4.99 |
| 74 | 9.40 | 8.82 | 8.28 | 7.77 | 7.29 | 6.83 | 6.45 | 6.09 | 5.74 | 5.41 |
| 73 | 10.02 | 9.44 | 8.89 | 8.38 | 7.89 | 7.43 | 7.01 | 6.60 | 6.21 | 5.84 |
| 72 | 11.10 | 10.43 | 9.79 | 9.19 | 8.63 | 8.09 | 7.62 | 7.17 | 6.74 | 6.33 |
| 71 | 12.10 | 11.36 | 10.67 | 10.02 | 9.40 | 8.82 | 8.31 | 7.82 | 7.36 | 6.92 |
| 70 | 13.36 | 12.52 | 11.72 | 10.98 | 10.27 | 9.60 | 9.03 | 8.49 | 7.97 | 7.48 |
| 69 | 14.60 | 13.67 | 12.79 | 11.97 | 11.19 | 10.45 | 9.82 | 9.23 | 8.66 | 8.11 |
| 68 | 16.00 | 14.96 | 13.99 | 13.07 | 12.20 | 11.37 | 10.68 | 10.02 | 9.39 | 8.78 |
| 67 | 17.50 | 16.35 | 15.27 | 14.26 | 13.30 | 12.39 | 11.61 | 10.86 | 10.15 | 9.47 |
| 66 | 19.00 | 17.76 | 16.60 | 15.51 | 14.47 | 13.49 | 12.64 | 11.83 | 11.05 | 10.31 |
| 65 | 21.00 | 19.59 | 18.26 | 17.01 | 15.82 | 14.70 | 13.76 | 12.86 | 12.01 | 11.19 |
| 64 | 23.00 | 21.43 | 19.96 | 18.57 | 17.25 | 16.00 | 14.98 | 14.00 | 13.06 | 12.16 |
| 63 | 25.10 | 23.38 | 21.77 | 20.24 | 18.80 | 17.44 | 16.31 | 15.24 | 14.22 | 13.24 |
| 62 | 27.60 | 25.66 | 23.84 | 22.13 | 20.51 | 18.97 | 17.73 | 16.55 | 15.42 | 14.34 |
| 61 | 30.33 | 28.17 | 26.14 | 24.23 | 22.42 | 20.71 | 19.37 | 18.10 | 16.88 | 15.72 |
| 60 | 33.47 | 31.05 | 28.78 | 26.64 | 24.62 | 22.70 | 21.24 | 19.84 | 18.50 | 17.23 |
| 59 | 37.00 | 34.31 | 31.77 | 29.39 | 27.13 | 24.99 | 23.37 | 21.83 | 20.36 | 18.95 |
| 58 | 41.00 | 38.00 | 35.18 | 32.52 | 30.00 | 27.61 | 25.82 | 24.11 | 22.47 | 20.90 |
| 57 | 45.30 | 41.99 | 38.88 | 35.95 | 33.18 | 30.54 | 28.59 | 26.72 | 24.94 | 23.24 |

58	Maintenance

Service Manual

| 56 | 50.20 | 46.55 | 43.12 | 39.89 | 36.83 | 33.93 | 31.76 | 29.69 | 27.71 | 25.82 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 55 | 56.00 | 51.92 | 48.08 | 44.47 | 41.05 | 37.80 | 35.35 | 33.02 | 30.79 | 28.65 |
| 54 | 62.80 | 58.20 | 53.88 | 49.80 | 45.95 | 42.29 | 39.51 | 36.87 | 34.34 | 31.92 |
| 53 | 70.00 | 64.95 | 60.21 | 55.74 | 51.51 | 47.50 | 44.33 | 41.31 | 38.42 | 35.65 |
| 52 | 78.80 | 73.12 | 67.79 | 62.76 | 58.00 | 53.49 | 49.86 | 46.40 | 43.10 | 39.94 |
| 51 | 88.00 | 81.79 | 75.97 | 70.47 | 65.27 | 60.34 | 56.11 | 52.08 | 48.23 | 44.54 |
| 50 | 99.10 | 92.12 | 85.57 | 79.39 | 73.55 | 68.00 | 63.15 | 58.52 | 54.10 | 49.86 |
| 49 | 111.00 | 103.28 | 96.04 | 89.20 | 82.74 | 76.61 | 70.94 | 65.54 | 60.38 | 55.44 |
| 48 | 126.20 | 117.27 | 108.88 | 100.97 | 93.48 | 86.38 | 79.89 | 73.71 | 67.79 | 62.13 |
| 47 | 142.60 | 132.48 | 122.97 | 114.00 | 105.52 | 97.48 | 90.16 | 83.18 | 76.51 | 70.12 |
| 46 | 162.00 | 150.38 | 139.46 | 129.16 | 119.43 | 110.19 | 101.62 | 93.45 | 85.64 | 78.17 |
| 45 | 185.00 | 171.49 | 158.81 | 146.85 | 135.53 | 124.80 | 115.00 | 105.66 | 96.74 | 88.20 |
| 44 | 212.00 | 196.23 | 181.41 | 167.45 | 154.23 | 141.70 | 130.18 | 119.19 | 108.69 | 98.64 |
| 43 | 243.00 | 224.65 | 207.41 | 191.15 | 175.78 | 161.19 | 148.03 | 135.48 | 123.49 | 112.01 |
| 42 | 280.00 | 258.38 | 238.08 | 218.93 | 200.82 | 183.64 | 168.64 | 154.32 | 140.65 | 127.56 |
| 41 | 324.00 | 298.37 | 274.29 | 251.59 | 230.12 | 209.75 | 192.53 | 176.11 | 160.43 | 145.41 |
| 40 | 375.30 | 344.95 | 316.43 | 289.55 | 264.12 | 240.00 | 220.30 | 201.52 | 183.57 | 166.39 |
| 39 | 431.00 | 395.97 | 363.07 | 332.05 | 302.71 | 274.87 | 251.94 | 230.08 | 209.19 | 189.19 |
| 38 | 500.00 | 458.51 | 419.54 | 382.80 | 348.04 | 315.07 | 289.04 | 264.21 | 240.49 | 217.78 |
| 37 | 580.00 | 531.11 | 485.18 | 441.88 | 400.92 | 362.06 | 332.09 | 303.52 | 276.21 | 250.07 |
| 36 | 676.00 | 618.14 | 563.79 | 512.55 | 464.08 | 418.09 | 383.52 | 350.57 | 319.07 | 288.92 |
| 35 | 790.00 | 721.80 | 657.74 | 597.34 | 540.20 | 486.00 | 445.77 | 407.41 | 370.75 | 335.66 |
| 34 | 930.00 | 848.96 | 772.84 | 701.08 | 633.19 | 568.78 | 521.38 | 476.19 | 433.01 | 391.66 |
| 33 | 1110.00 | 1011.10 | 918.19 | 830.60 | 747.75 | 669.14 | 613.58 | 560.59 | 509.97 | 461.49 |
| 32 | 1320.00 | 1201.45 | 1090.09 | 985.09 | 885.78 | 791.56 | 725.62 | 662.75 | 602.68 | 545.17 |
| 31 | 1590.00 | 1444.80 | 1308.40 | 1179.80 | 1058.15 | 942.75 | 863.43 | 787.81 | 715.55 | 646.36 |
| 30 | 1906.00 | 1731.91 | 1568.38 | 1414.20 | 1268.36 | 1130.00 | 1034.60 | 943.64 | 856.73 | 773.51 |
| 29 | 2300.00 | 2089.81 | 1892.37 | 1706.22 | 1530.13 | 1363.08 | 1244.55 | 1131.54 | 1023.56 | 920.17 |
| 28 | 2810.00 | 2550.31 | 2306.37 | 2076.38 | 1858.82 | 1652.43 | 1505.84 | 1366.07 | 1232.52 | 1104.65 |
| 27 | 3470.00 | 3144.23 | 2838.22 | 2549.70 | 2276.79 | 2017.87 | 1836.86 | 1664.27 | 1499.35 | 1341.45 |
| 26 | 4290.00 | 3885.50 | 3505.53 | 3147.28 | 2808.41 | 2486.92 | 2253.64 | 2031.21 | 1818.67 | 1615.18 |
| 25 | 5348.00 | 4843.01 | 4368.65 | 3921.40 | 3498.35 | 3097.00 | 2802.48 | 2521.66 | 2253.33 | 1996.42 |
| 24 | 6800.00 | 6152.28 | 5543.84 | 4970.19 | 4427.56 | 3912.77 | 3538.27 | 3181.20 | 2840.01 | 2513.33 |
| 23 | 8720.00 | 7888.61 | 7107.64 | 6371.32 | 5674.82 | 5014.05 | 4529.95 | 4068.38 | 3627.32 | 3205.04 |
| 22 | 11500.00 | 10371.38 | 9311.21 | 8311.65 | 7366.14 | 6469.15 | 5839.63 | 5239.39 | 4665.85 | 4116.71 |
| 21 | 15000.00 | 13512.80 | 12115.79 | 10798.65 | 9552.74 | 8370.76 | 7546.29 | 6760.17 | 6009.01 | 5289.82 |
| 20 | 19368.00 | 17441.37 | 15631.58 | 13925.26 | 12311.23 | 10780.00 | 9716.41 | 8702.31 | 7733.29 | 6805.52 |

HIS-06 temperature and humidity characteristic 25℃～ 34℃

Unit:KΩ

| Relative humidity | Temperature（℃） |
| --- | --- |
| %RH | 25℃ | 26℃ | 27℃ | 28℃ | 29℃ | 30℃ | 31℃ | 32℃ | 33℃ | 34℃ |
| 90 | 1.68 | 1.62 | 1.57 | 1.52 | 1.47 | 1.42 | 1.37 | 1.33 | 1.28 | 1.24 |
| 89 | 1.78 | 1.72 | 1.66 | 1.61 | 1.55 | 1.50 | 1.45 | 1.40 | 1.36 | 1.31 |
| 88 | 1.89 | 1.83 | 1.76 | 1.70 | 1.65 | 1.59 | 1.54 | 1.49 | 1.44 | 1.39 |
| 87 | 2.02 | 1.95 | 1.88 | 1.81 | 1.74 | 1.68 | 1.63 | 1.57 | 1.52 | 1.47 |
| 86 | 2.16 | 2.08 | 2.00 | 1.93 | 1.85 | 1.78 | 1.72 | 1.66 | 1.61 | 1.55 |
| 85 | 2.30 | 2.21 | 2.13 | 2.05 | 1.97 | 1.89 | 1.82 | 1.76 | 1.70 | 1.64 |
| 84 | 2.48 | 2.38 | 2.28 | 2.19 | 2.10 | 2.01 | 1.94 | 1.87 | 1.80 | 1.73 |
| 83 | 2.65 | 2.54 | 2.43 | 2.33 | 2.24 | 2.14 | 2.06 | 1.98 | 1.91 | 1.83 |
| 82 | 2.83 | 2.71 | 2.60 | 2.49 | 2.38 | 2.28 | 2.19 | 2.11 | 2.02 | 1.94 |
| 81 | 3.06 | 2.93 | 2.80 | 2.67 | 2.55 | 2.44 | 2.34 | 2.24 | 2.15 | 2.06 |
| 80 | 3.28 | 3.14 | 3.00 | 2.86 | 2.73 | 2.60 | 2.49 | 2.38 | 2.28 | 2.18 |
| 79 | 3.51 | 3.35 | 3.20 | 3.05 | 2.91 | 2.78 | 2.65 | 2.54 | 2.42 | 2.31 |
| 78 | 3.78 | 3.61 | 3.44 | 3.28 | 3.12 | 2.97 | 2.83 | 2.70 | 2.57 | 2.45 |
| 77 | 4.06 | 3.87 | 3.69 | 3.51 | 3.34 | 3.17 | 3.03 | 2.88 | 2.74 | 2.61 |
| 76 | 4.38 | 4.17 | 3.97 | 3.77 | 3.58 | 3.40 | 3.23 | 3.07 | 2.92 | 2.77 |
| 75 | 4.70 | 4.47 | 4.25 | 4.04 | 3.84 | 3.64 | 3.46 | 3.28 | 3.11 | 2.94 |
| 74 | 5.09 | 4.83 | 4.59 | 4.35 | 4.12 | 3.90 | 3.70 | 3.51 | 3.32 | 3.14 |

Maintenance	59

Service Manual

| 73 | 5.49 | 5.21 | 4.94 | 4.68 | 4.43 | 4.19 | 3.97 | 3.75 | 3.54 | 3.34 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 72 | 5.93 | 5.62 | 5.33 | 5.04 | 4.77 | 4.50 | 4.26 | 4.02 | 3.80 | 3.57 |
| 71 | 6.49 | 6.13 | 5.79 | 5.46 | 5.14 | 4.84 | 4.57 | 4.32 | 4.07 | 3.83 |
| 70 | 7.00 | 6.61 | 6.24 | 5.88 | 5.53 | 5.20 | 4.91 | 4.63 | 4.35 | 4.09 |
| 69 | 7.59 | 7.16 | 6.75 | 6.35 | 5.96 | 5.59 | 5.27 | 4.97 | 4.67 | 4.38 |
| 68 | 8.20 | 7.73 | 7.28 | 6.84 | 6.42 | 6.01 | 5.67 | 5.34 | 5.01 | 4.70 |
| 67 | 8.82 | 8.32 | 7.83 | 7.36 | 6.91 | 6.47 | 6.10 | 5.74 | 5.38 | 5.04 |
| 66 | 9.60 | 9.03 | 8.49 | 7.96 | 7.46 | 6.97 | 6.57 | 6.18 | 5.80 | 5.43 |
| 65 | 10.40 | 9.78 | 9.18 | 8.61 | 8.06 | 7.52 | 7.08 | 6.65 | 6.24 | 5.84 |
| 64 | 11.30 | 10.62 | 9.96 | 9.33 | 8.72 | 8.13 | 7.65 | 7.19 | 6.74 | 6.30 |
| 63 | 12.30 | 11.55 | 10.82 | 10.12 | 9.45 | 8.80 | 8.27 | 7.75 | 7.26 | 6.78 |
| 62 | 13.30 | 12.49 | 11.71 | 10.96 | 10.23 | 9.53 | 8.96 | 8.41 | 7.87 | 7.35 |
| 61 | 14.60 | 13.69 | 12.81 | 11.97 | 11.15 | 10.36 | 9.73 | 9.12 | 8.53 | 7.96 |
| 60 | 16.00 | 14.99 | 14.02 | 13.08 | 12.17 | 11.30 | 10.61 | 9.94 | 9.29 | 8.66 |
| 59 | 17.60 | 16.48 | 15.40 | 14.35 | 13.35 | 12.38 | 11.61 | 10.87 | 10.15 | 9.46 |
| 58 | 19.40 | 18.15 | 16.95 | 15.79 | 14.68 | 13.60 | 12.75 | 11.93 | 11.13 | 10.36 |
| 57 | 21.60 | 20.18 | 18.81 | 17.49 | 16.22 | 14.99 | 14.05 | 13.14 | 12.26 | 11.41 |
| 56 | 24.00 | 22.40 | 20.86 | 19.37 | 17.94 | 16.55 | 15.50 | 14.48 | 13.50 | 12.54 |
| 55 | 26.60 | 24.81 | 23.10 | 21.44 | 19.84 | 18.30 | 17.13 | 16.00 | 14.90 | 13.83 |
| 54 | 29.60 | 27.59 | 25.66 | 23.81 | 22.01 | 20.28 | 18.96 | 17.69 | 16.46 | 15.26 |
| 53 | 33.00 | 30.74 | 28.57 | 26.48 | 24.46 | 22.52 | 21.04 | 19.62 | 18.24 | 16.90 |
| 52 | 36.90 | 34.35 | 31.90 | 29.53 | 27.25 | 25.05 | 23.38 | 21.77 | 20.21 | 18.69 |
| 51 | 41.00 | 38.18 | 35.47 | 32.86 | 30.34 | 27.90 | 26.03 | 24.22 | 22.46 | 20.76 |
| 50 | 45.80 | 42.62 | 39.55 | 36.60 | 33.75 | 31.00 | 28.91 | 26.89 | 24.93 | 23.03 |
| 49 | 50.70 | 47.20 | 43.83 | 40.59 | 37.45 | 34.43 | 32.08 | 29.81 | 27.61 | 25.47 |
| 48 | 56.70 | 52.72 | 48.90 | 45.21 | 41.66 | 38.22 | 35.62 | 33.10 | 30.67 | 28.30 |
| 47 | 64.00 | 59.37 | 54.91 | 50.61 | 46.46 | 42.46 | 39.57 | 36.78 | 34.07 | 31.45 |
| 46 | 71.00 | 65.89 | 60.97 | 56.22 | 51.65 | 47.23 | 43.99 | 40.85 | 37.81 | 34.86 |
| 45 | 80.00 | 74.13 | 68.48 | 63.03 | 57.78 | 52.70 | 49.02 | 45.46 | 42.00 | 38.65 |
| 44 | 89.00 | 82.54 | 76.32 | 70.33 | 64.54 | 58.96 | 54.75 | 50.69 | 46.74 | 42.92 |
| 43 | 101.00 | 93.48 | 86.25 | 79.28 | 72.55 | 66.06 | 61.28 | 56.65 | 52.17 | 47.82 |
| 42 | 115.00 | 106.23 | 97.79 | 89.66 | 81.81 | 74.23 | 68.69 | 63.33 | 58.14 | 53.10 |
| 41 | 131.00 | 120.81 | 111.01 | 101.56 | 92.44 | 83.64 | 77.33 | 71.23 | 65.31 | 59.57 |
| 40 | 149.90 | 138.01 | 126.56 | 115.53 | 104.88 | 94.60 | 87.37 | 80.37 | 73.58 | 66.99 |
| 39 | 170.00 | 156.52 | 143.54 | 131.04 | 118.97 | 107.32 | 99.08 | 91.11 | 83.38 | 75.88 |
| 38 | 196.00 | 180.09 | 164.79 | 150.04 | 135.81 | 122.06 | 112.71 | 103.65 | 94.88 | 86.37 |
| 37 | 225.00 | 206.61 | 188.92 | 171.87 | 155.41 | 139.52 | 128.86 | 118.54 | 108.53 | 98.82 |
| 36 | 260.00 | 238.50 | 217.80 | 197.86 | 178.62 | 160.04 | 147.90 | 136.16 | 124.77 | 113.73 |
| 35 | 302.00 | 276.83 | 252.61 | 229.27 | 206.76 | 185.00 | 170.96 | 157.37 | 144.19 | 131.41 |
| 34 | 352.00 | 322.66 | 294.42 | 267.21 | 240.96 | 215.59 | 199.30 | 183.53 | 168.24 | 153.40 |
| 33 | 415.00 | 380.13 | 346.58 | 314.24 | 283.04 | 252.90 | 233.57 | 214.84 | 196.70 | 179.09 |
| 32 | 490.00 | 448.82 | 409.19 | 371.01 | 334.16 | 298.57 | 275.69 | 253.53 | 232.06 | 211.23 |
| 31 | 580.00 | 531.32 | 484.48 | 439.35 | 395.79 | 353.72 | 326.76 | 300.66 | 275.37 | 250.83 |
| 30 | 693.69 | 634.81 | 578.16 | 523.57 | 470.89 | 420.00 | 387.67 | 356.36 | 326.02 | 296.58 |
| 29 | 821.00 | 751.60 | 684.82 | 620.48 | 558.38 | 498.40 | 459.39 | 421.61 | 385.00 | 349.49 |
| 28 | 982.00 | 898.01 | 817.20 | 739.32 | 664.18 | 591.58 | 544.87 | 499.65 | 455.82 | 413.29 |
| 27 | 1190.00 | 1085.85 | 985.63 | 889.06 | 795.87 | 705.85 | 649.51 | 594.96 | 542.09 | 490.80 |
| 26 | 1420.00 | 1297.43 | 1179.49 | 1065.83 | 956.17 | 850.22 | 781.68 | 715.32 | 651.00 | 588.59 |
| 25 | 1750.00 | 1597.27 | 1450.30 | 1308.67 | 1172.02 | 1040.00 | 954.91 | 872.53 | 792.68 | 715.22 |
| 24 | 2200.00 | 2005.83 | 1818.99 | 1638.94 | 1465.21 | 1297.38 | 1189.66 | 1085.37 | 984.29 | 886.22 |
| 23 | 2800.00 | 2551.47 | 2312.32 | 2081.87 | 1859.50 | 1644.68 | 1506.06 | 1371.84 | 1241.75 | 1115.55 |
| 22 | 3590.00 | 3270.74 | 2963.54 | 2667.51 | 2381.86 | 2105.90 | 1925.97 | 1751.75 | 1582.89 | 1419.07 |
| 21 | 4600.00 | 4191.56 | 3798.54 | 3419.81 | 3054.38 | 2701.33 | 2467.06 | 2240.24 | 2020.39 | 1807.10 |
| 20 | 5915.63 | 5385.23 | 4874.84 | 4383.03 | 3908.47 | 3450.00 | 3152.84 | 2865.12 | 2586.25 | 2315.70 |

60	Maintenance

Service Manual

HIS-06 Characteristic of temperature and humidity 35℃ ~ 45℃

Unit:KΩ

| Relative humidity | Temperature（℃） |
| --- | --- |
| %RH | 35℃ | 36℃ | 37℃ | 38℃ | 39℃ | 40℃ | 41℃ | 42℃ | 43℃ | 44℃ | 45℃ |
| 90 | 1.20 | 1.17 | 1.14 | 1.11 | 1.08 | 1.05 | 1.02 | 1.00 | 0.98 | 0.95 | 0.93 |
| 89 | 1.27 | 1.23 | 1.20 | 1.16 | 1.13 | 1.10 | 1.07 | 1.05 | 1.02 | 1.00 | 0.97 |
| 88 | 1.34 | 1.30 | 1.26 | 1.22 | 1.19 | 1.15 | 1.12 | 1.09 | 1.07 | 1.04 | 1.02 |
| 87 | 1.42 | 1.37 | 1.33 | 1.29 | 1.25 | 1.21 | 1.18 | 1.15 | 1.12 | 1.09 | 1.06 |
| 86 | 1.50 | 1.45 | 1.40 | 1.36 | 1.31 | 1.27 | 1.24 | 1.20 | 1.17 | 1.14 | 1.11 |
| 85 | 1.58 | 1.53 | 1.48 | 1.43 | 1.38 | 1.33 | 1.29 | 1.26 | 1.23 | 1.19 | 1.16 |
| 84 | 1.67 | 1.61 | 1.56 | 1.50 | 1.45 | 1.40 | 1.36 | 1.32 | 1.29 | 1.25 | 1.21 |
| 83 | 1.76 | 1.70 | 1.64 | 1.58 | 1.52 | 1.47 | 1.43 | 1.39 | 1.35 | 1.31 | 1.27 |
| 82 | 1.86 | 1.79 | 1.73 | 1.66 | 1.60 | 1.54 | 1.50 | 1.45 | 1.41 | 1.37 | 1.33 |
| 81 | 1.97 | 1.90 | 1.82 | 1.75 | 1.69 | 1.62 | 1.57 | 1.53 | 1.48 | 1.44 | 1.40 |
| 80 | 2.08 | 2.00 | 1.93 | 1.85 | 1.78 | 1.71 | 1.66 | 1.61 | 1.56 | 1.51 | 1.46 |
| 79 | 2.20 | 2.12 | 2.03 | 1.95 | 1.88 | 1.80 | 1.74 | 1.69 | 1.64 | 1.59 | 1.54 |
| 78 | 2.33 | 2.24 | 2.15 | 2.07 | 1.98 | 1.90 | 1.84 | 1.78 | 1.72 | 1.67 | 1.61 |
| 77 | 2.48 | 2.38 | 2.28 | 2.18 | 2.09 | 2.00 | 1.94 | 1.87 | 1.81 | 1.75 | 1.69 |
| 76 | 2.62 | 2.51 | 2.41 | 2.31 | 2.21 | 2.12 | 2.05 | 1.98 | 1.91 | 1.84 | 1.78 |
| 75 | 2.78 | 2.67 | 2.56 | 2.45 | 2.34 | 2.24 | 2.16 | 2.09 | 2.01 | 1.94 | 1.87 |
| 74 | 2.96 | 2.84 | 2.71 | 2.60 | 2.48 | 2.37 | 2.29 | 2.20 | 2.12 | 2.04 | 1.97 |
| 73 | 3.14 | 3.01 | 2.88 | 2.75 | 2.63 | 2.51 | 2.42 | 2.33 | 2.24 | 2.15 | 2.07 |
| 72 | 3.36 | 3.21 | 3.06 | 2.92 | 2.78 | 2.65 | 2.55 | 2.46 | 2.36 | 2.27 | 2.18 |
| 71 | 3.60 | 3.44 | 3.28 | 3.12 | 2.97 | 2.82 | 2.71 | 2.61 | 2.50 | 2.40 | 2.30 |
| 70 | 3.83 | 3.65 | 3.48 | 3.32 | 3.16 | 3.00 | 2.88 | 2.77 | 2.65 | 2.54 | 2.43 |
| 69 | 4.10 | 3.91 | 3.73 | 3.55 | 3.37 | 3.20 | 3.07 | 2.94 | 2.82 | 2.70 | 2.58 |
| 68 | 4.40 | 4.19 | 3.99 | 3.79 | 3.60 | 3.41 | 3.27 | 3.13 | 2.99 | 2.86 | 2.73 |
| 67 | 4.71 | 4.49 | 4.27 | 4.06 | 3.85 | 3.65 | 3.49 | 3.34 | 3.19 | 3.05 | 2.90 |
| 66 | 5.08 | 4.83 | 4.59 | 4.36 | 4.13 | 3.91 | 3.74 | 3.57 | 3.41 | 3.25 | 3.09 |
| 65 | 5.45 | 5.19 | 4.93 | 4.68 | 4.44 | 4.20 | 4.01 | 3.83 | 3.65 | 3.47 | 3.30 |
| 64 | 5.88 | 5.59 | 5.31 | 5.04 | 4.78 | 4.52 | 4.31 | 4.11 | 3.91 | 3.72 | 3.53 |
| 63 | 6.31 | 6.00 | 5.70 | 5.41 | 5.13 | 4.85 | 4.63 | 4.41 | 4.20 | 4.00 | 3.80 |
| 62 | 6.84 | 6.50 | 6.17 | 5.84 | 5.53 | 5.22 | 4.98 | 4.75 | 4.52 | 4.30 | 4.09 |
| 61 | 7.40 | 7.03 | 6.66 | 6.31 | 5.97 | 5.63 | 5.37 | 5.12 | 4.88 | 4.64 | 4.41 |
| 60 | 8.05 | 7.64 | 7.24 | 6.86 | 6.48 | 6.11 | 5.83 | 5.55 | 5.28 | 5.01 | 4.76 |
| 59 | 8.78 | 8.33 | 7.89 | 7.46 | 7.05 | 6.64 | 6.33 | 6.02 | 5.72 | 5.43 | 5.14 |
| 58 | 9.61 | 9.10 | 8.61 | 8.13 | 7.66 | 7.20 | 6.86 | 6.52 | 6.19 | 5.87 | 5.56 |
| 57 | 10.58 | 10.00 | 9.43 | 8.88 | 8.34 | 7.82 | 7.44 | 7.08 | 6.72 | 6.36 | 6.02 |
| 56 | 11.61 | 10.96 | 10.33 | 9.71 | 9.11 | 8.53 | 8.11 | 7.70 | 7.30 | 6.91 | 6.53 |
| 55 | 12.80 | 12.07 | 11.36 | 10.68 | 10.00 | 9.35 | 8.88 | 8.42 | 7.97 | 7.53 | 7.10 |
| 54 | 14.10 | 13.29 | 12.50 | 11.73 | 10.98 | 10.25 | 9.72 | 9.21 | 8.70 | 8.21 | 7.73 |
| 53 | 15.60 | 14.68 | 13.78 | 12.90 | 12.05 | 11.22 | 10.63 | 10.06 | 9.50 | 8.96 | 8.42 |
| 52 | 17.22 | 16.18 | 15.18 | 14.20 | 13.24 | 12.31 | 11.66 | 11.02 | 10.40 | 9.79 | 9.19 |
| 51 | 19.10 | 17.93 | 16.79 | 15.68 | 14.59 | 13.54 | 12.81 | 12.10 | 11.40 | 10.72 | 10.05 |
| 50 | 21.18 | 19.87 | 18.60 | 17.36 | 16.15 | 14.97 | 14.14 | 13.33 | 12.54 | 11.77 | 11.01 |
| 49 | 23.40 | 21.97 | 20.57 | 19.21 | 17.89 | 16.60 | 15.65 | 14.73 | 13.82 | 12.94 | 12.08 |
| 48 | 26.00 | 24.35 | 22.75 | 21.20 | 19.68 | 18.20 | 17.17 | 16.16 | 15.18 | 14.21 | 13.27 |
| 47 | 28.90 | 27.06 | 25.28 | 23.54 | 21.85 | 20.20 | 19.03 | 17.88 | 16.77 | 15.68 | 14.61 |
| 46 | 32.00 | 29.95 | 27.96 | 26.03 | 24.14 | 22.30 | 21.00 | 19.74 | 18.50 | 17.29 | 16.11 |
| 45 | 35.40 | 33.16 | 30.99 | 28.87 | 26.81 | 24.80 | 23.33 | 21.90 | 20.50 | 19.14 | 17.80 |
| 44 | 39.20 | 36.71 | 34.29 | 31.93 | 29.64 | 27.40 | 25.79 | 24.21 | 22.67 | 21.17 | 19.70 |

Maintenance	61

Service Manual

| 43 | 43.60 | 40.77 | 38.02 | 35.35 | 32.74 | 30.20 | 28.45 | 26.73 | 25.06 | 23.43 | 21.83 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42 | 48.20 | 45.06 | 42.00 | 39.02 | 36.13 | 33.30 | 31.40 | 29.55 | 27.74 | 25.97 | 24.25 |
| 41 | 54.00 | 50.43 | 46.97 | 43.59 | 40.30 | 37.10 | 34.98 | 32.92 | 30.90 | 28.93 | 27.00 |
| 40 | 60.60 | 56.63 | 52.78 | 49.02 | 45.36 | 41.80 | 39.36 | 36.98 | 34.66 | 32.39 | 30.17 |
| 39 | 68.60 | 64.04 | 59.61 | 55.30 | 51.10 | 47.00 | 44.23 | 41.53 | 38.89 | 36.31 | 33.78 |
| 38 | 78.10 | 72.70 | 67.45 | 62.33 | 57.35 | 52.50 | 49.44 | 46.45 | 43.54 | 40.69 | 37.90 |
| 37 | 89.40 | 82.99 | 76.75 | 70.68 | 64.76 | 59.00 | 55.58 | 52.24 | 48.98 | 45.80 | 42.68 |
| 36 | 103.00 | 95.43 | 88.06 | 80.89 | 73.91 | 67.10 | 63.17 | 59.33 | 55.59 | 51.93 | 48.35 |
| 35 | 119.00 | 110.35 | 101.94 | 93.75 | 85.77 | 78.00 | 73.18 | 68.47 | 63.88 | 59.39 | 55.00 |
| 34 | 139.00 | 129.32 | 119.90 | 110.73 | 101.80 | 93.10 | 86.80 | 80.66 | 74.66 | 68.80 | 63.07 |
| 33 | 162.00 | 149.97 | 138.28 | 126.90 | 115.81 | 105.00 | 98.24 | 91.63 | 85.19 | 78.89 | 72.73 |
| 32 | 191.00 | 176.44 | 162.29 | 148.50 | 135.08 | 122.00 | 114.10 | 106.40 | 98.87 | 91.52 | 84.34 |
| 31 | 227.00 | 209.28 | 192.04 | 175.27 | 158.93 | 143.00 | 133.62 | 124.46 | 115.52 | 106.79 | 98.25 |
| 30 | 268.00 | 247.75 | 228.05 | 208.88 | 190.20 | 172.00 | 160.04 | 148.37 | 136.97 | 125.83 | 114.95 |
| 29 | 315.00 | 291.16 | 267.97 | 245.41 | 223.43 | 202.00 | 187.96 | 174.26 | 160.88 | 147.81 | 135.03 |
| 28 | 372.00 | 342.25 | 313.32 | 285.16 | 257.73 | 231.00 | 215.94 | 201.25 | 186.90 | 172.88 | 159.17 |
| 27 | 441.00 | 404.50 | 369.01 | 334.45 | 300.80 | 268.00 | 251.39 | 235.18 | 219.35 | 203.88 | 188.76 |
| 26 | 528.00 | 484.54 | 442.27 | 401.13 | 361.06 | 322.00 | 301.66 | 281.81 | 262.43 | 243.49 | 224.98 |
| 25 | 640.00 | 590.21 | 541.79 | 494.65 | 448.75 | 404.00 | 375.91 | 348.49 | 321.72 | 295.57 | 270.00 |
| 24 | 791.00 | 735.73 | 681.97 | 629.64 | 578.68 | 529.00 | 486.67 | 445.36 | 405.02 | 365.60 | 327.08 |
| 23 | 993.00 | 926.97 | 862.74 | 800.23 | 739.35 | 680.00 | 621.22 | 563.85 | 507.84 | 453.11 | 399.61 |
| 22 | 1260.00 | 1171.18 | 1084.80 | 1000.72 | 918.82 | 839.00 | 766.05 | 694.86 | 625.34 | 557.42 | 491.03 |
| 21 | 1600.00 | 1476.79 | 1356.97 | 1240.33 | 1126.73 | 1016.00 | 929.53 | 845.14 | 762.74 | 682.23 | 603.53 |
| 20 | 2053.00 | 1880.43 | 1712.58 | 1549.22 | 1390.09 | 1235.00 | 1131.26 | 1030.03 | 931.17 | 834.59 | 740.18 |

62	Maintenance

REGULATION (EU) N. 517/2014 - F-GAS

The unit contains R290, a natural greenhouse gas with global warming potential (GWP) = 3 DRY PURY 11 : Kg. 0,045 = 0,000135 Tonn CO2 equiv

DRY PURY 13 : Kg. 0,045 = 0,000135 Tonn CO2 equiv DRY PURY 17 : Kg. 0,050 = 0,000015 Tonn CO2 equiv DRY PURY 21 : Kg. 0,080 = 0,000240 Tonn CO2 equiv DRY PURY 25 : Kg. 0,075 = 0,000225 Tonn CO2 equiv

Do not release R290 into the atmosphere.

INFORMATION FOR THE CORRECT DISPOSAL OF THE PRODUCT IN ACCORDANCE WITH EUROPEAN DIRECTIVE 2012/19/EU

This appliance may not be scrapped with domestic waste at the end of its life cycle. We call your attention to the crucial role played by the consumer in the re-use, recycling and other forms of recovery of such waste.

The appliance must be scrapped by a sorted waste disposal centre or by returning it to the retailer (no charge is levied for this service), when you purchase a new equivalent appliance.

Sorted disposal of electric and electronic equipment prevents the negative effects on the environment and human health resulting from improper scrapping, and also allows the materials from which it is made to be recovered and recycled, with significant savings in terms of energy and resources.

The sorted disposal requirement is indicated by the crossed waste bin label affixed to the appliance.

www.argoclima.com

# Text boxes

EN

DEHUMIDIFIER

SERVICE MANUAL

This is a specific remark and points out the importance of a specific section

ONLY original spare-parts are permitted for Service and Re- pair!

Proceed according the manuals Instructions!

Pay attention to the room size for indoor unit installation!

For specific in- formation refer page XXX of this manual.

Get your Best Practices knowledge and skills update for HC refrigerants and be certificated for these jobs!

Read More! SAFETY CODE OF PRACTICE FOR REFRIGE- RATING SYS- TEMS UTILISING A2 & A3 REFRIGE- RANTS

ISBN

1 872719 15 5

HC R-290 refrig- erant has a high grade of purity.

Propane as a cooking gas is not useful for refrigeration purpose!

| Molecular formula | C3H8 |
| --- | --- |
| Melting point [°C] | -188 |
| Boiling point under atmospheric pressure [°C] | -42 |
| Molar mass [g mol -1] | 44,10 |
| Critical temperature [ °C] | 96,8 |
| Critical pressure [bar] | 42 |
| Practical limit [g/m3 ] | 8 |
| Lower flammability level LFL [g/m3 ] | 38 |
| Lower flammability level LFL [ %] | 2,1 |
| Upper flammability level UFL [ g/m3] | 171 |
| Upper flammability level UFL [ %] | 9,5 |
| Ignition temperature [ °C] | 470 |

Read More!

Guidlines for the safe use of hydro- carbon refrige- rants

GIZ—PROKLIMA

http://www.gtz.de/ proklima

To ignite HC R- 290, three (3) components must exist at the same time at work area

to cause the refrigerant burning!

1 kg of liquid HC R-290 refrigerant creates about 250 litres of gas

Beside the flam- mability, most other safety properties are similar to other refrigerants!

Rely always on best service practices in refrigeration!

The HC leak de- tector is indeed a Personal Protective Equipment (PPE)

device!

The HC leak de- tector is indeed a PPE device!

405

487

482

M

+80,',7< 6(1625

67

0

352;,0,7<

6:,7&+

)$1 02725

5'

%1	&

7(03 +80

$3 ',63/$<

&1

)$1

',63

$& /

.

%2$5'

',63

$3

78%(

0$,1

%2$5'

1

&203

%1 %.

%8 :+

<(*1 *1

/

1

57

5'

%8

32:(5

3(

78%(

7(03 6(1625

&

&203

<(*1

&203

3(

600007064609

2

3

4

5

6

| No. | Name |
| --- | --- |
| 1 | Fan(reserve medium fan speed) |
| 2 | Neutral wire |
| 3 | Compressor |
| 4 | Live wire |
| 5 | Interface of display board |
| 6 | Water level terminal |

6

Filter cleaning indicator

Timer indicator

High fan speed

Low fan speed

Auto Button

Timer Button

Fan Button

Power Button

2

4

5

6

7

Refrigerant Safety Precautions:

Improper installation may lead to fire hazard explosion,

electric shock or injury.

Electrical Safety Precautions:

Concentration detector

Leakage test for the complete unit

Remove panel

Remove front case

The qualified parts provided by manufacturer

Replace electric box

End

Leakage

no

yes

Concentration detector

Leakage test for the complete unit

Remove panel

Remove front case

The qualified parts provided by manufacturer

Replace main board

Leakage

no

yes

Remove the

shielding box of electric box

Insert the temperature sensor tightly

Make the parts upright

Replace it with a temperature sensor of the same model

Replace the controller with one of the same model

Start

Is the wiring

terminal between temperature sensor and the controller loosened or

poor ly contacted?

yes

no

no

Malfunction is

eliminated.

Is there short circuit due to trip over

of the par ts?

yes

no

no

Malfunction is eliminated.

yes

Is the temperature

sensor  normal according to the Resistance Table?

no

yes

yes

no

Malfunction is removed.

yes

End

check the connection

Eliminate short circuit phenomenon

Replace the humidity sensor board

Replace the display board with the same model

Trouble shooting for malfunction

of humidity sensor

Humidity sensor is not

connected well with mainboard

yes

no

no

Is malfunction

eliminated?

The foot of humidity sensor

is short-circuit or the display board is short circuit

yes

no

no

Is malfunction

eliminated?

yes

Is the humidity

sensor normal according to the

Resistance Table?

no

yes

no

Is malfunction

eliminated?

yes

yes

End

Clean the heat exchangers and remove blockage of air inlet/outlet.

Insert the evaporator sensor tightly

Replace a main board with the same model.

Troubleshooting

for F0 malfunction

Check whether the

refrigerant is leaking?

yes

no

Heat exchangers are

too dirty or the air inlet/outlet is blocked.

yes

Malfunction is eliminated.

yes

no

no

evaporator sensor is inserted

tightly?

yes

Malfunction is eliminated.

yes

no

no

End

Clean the heat exchangers and remove blockage of air inlet/outlet.

Check motor and re-install the moto to make it run normally.

Make compressor run normally.

Replace a display board with the same model.

Start

Heat exchangers are

too dirty or the air inlet/outlet is blocked.

yes

Malfunction is eliminated.

yes

no

no

Abnormal fan speed; fan speed is too low

or the fan doesn't run.

yes

Malfunction is eliminated.

yes

no

no

normally. Strange noise or leakage occurs.

Casing is too hot.

yes

Malfunction is eliminated.

yes

no

no

End

31

32

33

34

4

3

2

56

55

54

53

52

51

50

49

48

35

36

1

37

38

39

47

46

45

44

43

40

41

42

| Fahrenheit display temperature （℉） | Fahrenheit （℉） | Celsius（℃ | ） | Fahrenheit display temperature （℉） | Fahrenheit （℉） | Celsius（℃ | ） | Fahrenheit display temperature （℉） | Fahrenheit （℉） | Celsius（℃ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 61 | 60.8 | 16 |  | 69/70 | 69.8 | 21 |  | 78/79 | 78.8 | 26 |
| 62/63 | 62.6 | 17 |  | 71/72 | 71.6 | 22 |  | 80/81 | 80.6 | 27 |
| 64/65 | 64.4 | 18 |  | 73/74 | 73.4 | 23 |  | 82/83 | 82.4 | 28 |
| 66/67 | 66.2 | 19 |  | 75/76 | 75.2 | 24 |  | 84/85 | 84.2 | 29 |
| 68 | 68 | 20 |  | 77 | 77 | 25 |  | 86 | 86 | 30 |

| Fahrenheit display temperature （℉） | Fahrenheit （℉） | Celsius（℃ | ） | Fahrenheit display temperature （℉） | Fahrenheit （℉） | Celsius（℃ | ） | Fahrenheit display temperature （℉） | Fahrenheit （℉） | Celsius（℃ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 32/33 | 32 | 0 |  | 55/56 | 55.4 | 13 |  | 79/80 | 78.8 | 26 |
| 34/35 | 33.8 | 1 |  | 57/58 | 57.2 | 14 |  | 81 | 80.6 | 27 |
| 36 | 35.6 | 2 |  | 59/60 | 59 | 15 |  | 82/83 | 82.4 | 28 |
| 37/38 | 37.4 | 3 |  | 61/62 | 60.8 | 16 |  | 84/85 | 84.2 | 29 |
| 39/40 | 39.2 | 4 |  | 63 | 62.6 | 17 |  | 86/87 | 86 | 30 |
| 41/42 | 41 | 5 |  | 64/65 | 64.4 | 18 |  | 88/89 | 87.8 | 31 |
| 43/44 | 42.8 | 6 |  | 66/67 | 66.2 | 19 |  | 90 | 89.6 | 32 |
| 45 | 44.6 | 7 |  | 68/69 | 68 | 20 |  | 91/92 | 91.4 | 33 |
| 46/47 | 46.4 | 8 |  | 70/71 | 69.8 | 21 |  | 93/94 | 93.2 | 34 |
| 48/49 | 48.2 | 9 |  | 72 | 71.6 | 22 |  | 95/96 | 95 | 35 |
| 50/51 | 50 | 10 |  | 73/74 | 73.4 | 23 |  | 97/98 | 96.8 | 36 |
| 52/53 | 51.8 | 11 |  | 75/76 | 75.2 | 24 |  | 99 | 98.6 | 37 |
| 54 | 53.6 | 12 |  | 77/78 | 77 | 25 |  |  |  |  |

| 38 | 1128.50 | 1033.61 | 953.39 | 883.90 | 822.61 | 767.78 | 704.83 | 647.37 | 594.51 | 545.56 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 37 | 1325.87 | 1213.40 | 1118.31 | 1035.94 | 963.29 | 898.30 | 823.48 | 755.17 | 692.34 | 634.16 |
| 36 | 1563.51 | 1430.14 | 1317.38 | 1219.71 | 1133.55 | 1056.48 | 967.04 | 885.39 | 810.28 | 740.74 |
| 35 | 1855.67 | 1695.83 | 1560.69 | 1443.63 | 1340.37 | 1248.00 | 1140.34 | 1042.06 | 951.64 | 867.93 |
| 34 | 2213.60 | 2020.33 | 1856.92 | 1715.37 | 1590.51 | 1478.82 | 1349.81 | 1232.04 | 1123.70 | 1023.39 |
| 33 | 2665.63 | 2426.92 | 2225.10 | 2050.27 | 1896.06 | 1758.12 | 1605.77 | 1466.69 | 1338.74 | 1220.28 |
| 32 | 3230.73 | 2933.36 | 2681.95 | 2464.17 | 2272.06 | 2100.23 | 1916.82 | 1749.39 | 1595.37 | 1452.76 |
| 31 | 3962.78 | 3585.59 | 3266.69 | 2990.44 | 2746.77 | 2528.80 | 2308.12 | 2106.66 | 1921.33 | 1749.74 |
| 30 | 4915.40 | 4431.65 | 4022.65 | 3668.35 | 3355.84 | 3076.30 | 2801.20 | 2550.06 | 2319.03 | 2105.13 |
| 29 | 6180.16 | 5548.66 | 5014.73 | 4552.22 | 4144.26 | 3779.32 | 3431.59 | 3114.13 | 2822.10 | 2551.72 |
| 28 | 7874.08 | 7035.10 | 6325.74 | 5711.27 | 5169.27 | 4684.43 | 4243.82 | 3841.57 | 3471.54 | 3128.95 |
| 27 | 10162.49 | 9029.08 | 8070.80 | 7240.70 | 6508.50 | 5853.53 | 5293.25 | 4781.75 | 4311.22 | 3875.57 |
| 26 | 13243.42 | 11702.63 | 10399.92 | 9271.46 | 8276.08 | 7385.69 | 6658.01 | 5993.68 | 5382.56 | 4816.75 |
| 25 | 17366.01 | 15270.67 | 13499.09 | 11964.48 | 10610.86 | 9400.00 | 8447.52 | 7577.98 | 6778.07 | 6037.48 |
| 24 | 22845.46 | 20023.30 | 17637.20 | 15570.26 | 13747.10 | 12116.22 | 10866.57 | 9725.72 | 8676.25 | 7704.59 |
| 23 | 30130.06 | 26367.98 | 23187.18 | 20431.85 | 18001.48 | 15827.43 | 14156.73 | 12631.50 | 11228.43 | 9929.38 |
| 22 | 39673.45 | 34712.87 | 30518.76 | 26885.65 | 23681.03 | 20814.39 | 18624.92 | 16626.08 | 14787.33 | 13084.91 |
| 21 | 51880.00 | 45447.42 | 40008.75 | 35297.56 | 31142.00 | 27424.72 | 24504.12 | 21837.82 | 19385.06 | 17114.16 |
| 20 | 68057.37 | 59623.21 | 52492.24 | 46315.10 | 40866.49 | 35992.53 | 32084.71 | 28517.14 | 25235.30 | 22196.79 |